# Supplementary Figures

Fig. 5 Two clustering quality indicators of different number of typical days (a); Heating demand error in load duration curve for the anchor building (b)

Fig. 6 Simulated energy demand (heating and electricity) for all buildings (stacked) in the district corresponding to the 13 typical days (colors represent the different buildings in the district)

Fig. 12 Linear cost curve over pipe capacity

# Appendix

## Appendix A.

In this appendix, the formulations of the constraints for other generation technologies (CHP, PV, ST, Gas Boiler, Biomass Boiler, GSHP) and storage technologies (battery and thermal storage) in the optimization model are given.

Solar technologies:

Solar technologies considered in the model include both PV panels and solar thermal panels. The installed capacities are represented as the installed area  AiPVand AiST at each building i. The upper bound of the total installed capacity of solar technologies is limited by the available roof area, shown in Eq.A.1.

AiPV+AiST≤Airoof ∀ i#A.1

Output power from the PV panels at every timestep is calculated as:

Pi,tPV=ηPV∙AiPV∙ItSolar ∀ i, t #A.2

Output power from the Solar Thermal panels at every timestep is calculated as:

Pi,tST=ηST∙AiST∙ItSolar ∀ i, t #A.3

Storage technologies:

Storage technologies include battery storage and thermal storage. The operational constraints are set up for storage technologies concerning their state of charge (SOC), standby, discharging, and charging performances. In this model, storage technologies are considered only for daily storage usage. Therefore, the energy stored at the beginning of the day should equal to the state at the end of the day for each typical day. To achieve this, the state of charge in the storage technology represented in Eq.A.4 applies to the first time step of the day, and Eq.A.5 applies for the rest of the timesteps of the day.

SOCi,t=1-sl∙SOCi,t+23+ηcha∙Pi,tcha-Pi,tdischaηdischa ∀ i, t #A.4

SOCi,t=1-sl∙SOCi,t-1+ηcha∙Pi,tcha-Pi,tdischaηdischa ∀ i, t #A.5

Dispatchable conversion technologies:

The dispatchable conversion technologies include boilers (gas boilers and biomass boilers), CHP, and GSHP. For each technology, there is a lower bound for the installed capacity. The operations of the technologies are assumed by a linear curve. Detailed values used for the technical specifications are given in Table B. 1 in Appendix B. A minimum load constraint is set as 15% for the boilers. This is formulated by using a binary variable (δop,i,tGB δop,i,tBB) to guarantee the operations of the boilers within the bound of the minimum load requirement, as shown in Eq.A.6-9.

Pi,tGB≤δop,i,tGB∙M  ∀ i, t #A.6

ζminGB∙CapiGB≤Pi,tGB+M∙1-δop,i,tGB ∀ i, t #A.7

Pi,tBB≤δop,i,tBB∙M  ∀ i, t #A.8

ζminBB∙CapiBB≤Pi,tBB+M∙1-δop,i,tBB ∀ i, t #A.9

The input of each energy carriers (natural gas, biomass) to the D-MES is calculated according to the operational performance of each conversion technologies as :

Pi,tCHPηCHP,el+Pi,tGBηGB=Ii,tGas ∀ i, t #A.10

Pi,tBBηBB=Ii,tBiomass ∀ i, t #A.11

Appendix B.

In this appendix, all values used for the technical parameters, costs, and emission data in the optimization models (a-d) are given.

Table B. 1 Investment costs and technical specifications of energy conversion technologies.

| Energy Conversion technology | Fixed Investment cost (CHF)[a] | Linear Investment cost (CHF/kW) [a] | Efficiency (%)¦COP [b] | Lifetime (year) [b] | Minimum load (%) | Minimum Capacity (kW¦m2) |
| --- | --- | --- | --- | --- | --- | --- |
| Gas Boiler | 27600 | 620 | 90 | 25 | 15 | 20 |
| Biomass Boiler | 27800 | 860 | 85 | 25 | 15 | 20 |
| CHP | 43450 | 3100 | ηCHP,el :25% HER: 2 | 20 | - | 20 |
| GSHP | 20000 | 2380 | COP:4 | 20 | - | 20 |
| ST panels | 4000 | 1000 | 45 | 25 | - | 1 |
| PV panels | 900 | 400 | 15 | 30 | - | 1 |

a:(M.Jakob, S. Kallio, W. Otto, C.Nägeli, R. Bolliger, 2015) b: (Morvaj et al., 2016)

Table B. 2 Investment costs and technical specifications of storage technologies (Mavromatidis, 2017)

| Storage Technologies | Fixed Investment cost (CHF)[a] | Linear Investment cost (CHF/kWh)[a] | Lifetime (year) [b] | Standby loss (%/hour) [b] | Charging & Discharging efficiency (%) [b] |
| --- | --- | --- | --- | --- | --- |
| Battery | 2000 | 600 | 10 | 0.1 | 90/90 |
| TES | 1685 | 12.5 | 30 | 0.1 | 99/99 |

Table B. 3 Fuel price, electricity price and carbon emissions for each energy carrier (Mavromatidis, 2017)

| Energy carrier | Price (CHF/kWh) | CO2 (kg CO2-eq/kWh) |
| --- | --- | --- |
| Natural Gas | 0.12 | 0.198 |
| Biomass | 0.127 | 0 |
| Electricity | 0.237¦ Feed-in tariff 0.0798 | 0.0095 |

Appendix C:

This appendix includes information and parameters related to the thermal network's assumptions. In the DHN simulation model, the thermal transfer coefficient kij is  approximated as a linear function depends on the pipe diameter based on extrapolated data from Liu et al. (Liu et al., 2015) as : kij=0.1495+0.0014∙dij. The pipe roughness ε is 0.4 mm. Ground temperature Tg  is assumed as constant at 10 °C. In the MILP optimization model (b-d), the new derived thermal loss coefficient kijlinear=a+b∙Capijpipe, and a=0.172 x 10-3 and b=7.69x10-8 .

Table C. 1 Data for Piping costs according to the design diameter used in the DHN simulation model (Nussbaumer and Thalmann, 2016)

| Nominal Diameter (mm) | Piping cost (€/m) | Trench cost (€/m) | Total costs (€/m) |
| --- | --- | --- | --- |
| 20 | 226 | 83 | 308 |
| 25 | 231 | 83 | 313 |
| 32 | 257 | 83 | 340 |
| 40 | 272 | 83 | 355 |
| 50 | 293 | 107 | 400 |
| 65 | 335 | 107 | 442 |
| 80 | 376 | 124 | 500 |
| 100 | 504 | 140 | 645 |
| 125 | 640 | 157 | 798 |
| 150 | 791 | 165 | 956 |
| 200 | 960 | 182 | 1141 |
| 250 | 1363 | 207 | 1569 |

(Exchange rate 1.13 is used to convert Euros into Swiss Francs.)

Table C. 2 Data for Piping costs and lifetime used in the optimization model (a-d)

|  | Model (a) (Morvaj et al., 2016) | Model (b-d) |  | Model (a-d) (Morvaj et al., 2016) |
| --- | --- | --- | --- | --- |
| District Heating Network | Fixed Investment cost (CHF/m) | Fixed Investment cost (CHF/m) | Linear Investment cost (CHF/kW/m) | Lifetime (year) |
| Pipe capacity < 657 kW | 400 | 327 | 0.189 | 40 |
| Pipe capacity > 657 kW | 400 | 392 | 0.089 | 40 |

# References:

Liu, X., Jenkins, N., Wu, J., and Bagdanavicius, A. (2015). Combined analysis of electricity and heat networks. Appl. Energy 61, 155–159. doi:10.1016/j.egypro.2014.11.928.

M.Jakob, S. Kallio, W. Otto, C.Nägeli, R. Bolliger, S. V. G. (2015). INSPIRE-Tool. TEP Energy GmbH & econcept AG. Available at: http://www.inspire-tool.ch.

Mavromatidis, G. (2017). Model-based design of distributed urban energy systems under uncertainty.

Morvaj, B., Evins, R., and Carmeliet, J. (2016). Optimising urban energy systems: Simultaneous system sizing, operation and district heating network layout. Energy 116, 619–636. doi:10.1016/j.energy.2016.09.139.

Nussbaumer, T., and Thalmann, S. (2016). Influence of system design on heat distribution costs in district heating. Energy 101, 496–505. doi:10.1016/j.energy.2016.02.062.