## WWTPs inventory
rptMStateKey | uwwNuts | aggCode | uwwCode | uwwName | uwwLatitude | uwwLongitude | uwwCapacity | uwwLoadEntering | anaerobic digestion [y/n] | inflow [m³/h] | digester gas [m³/d] | digester gas el. [MWh/a] | digester gas th. [MWh/a] | heat recovery potential [kW] | heat pump [MWh/a] | NUTS_ID | spatial context
AT | AT113 | ATAG_1-00000036 | ATTP_1-00000036 | Mischendorf | 47.1862 | 16.3465 | 5000 | 3931 | NO | 24.5687 | 0 | 0 | 0 | 142.4987 | 854.9925 | AT11 | B
AT | AT112 | ATAG_1-W1 | ATTP_1-W1 | Wimpassing/Leitha | 47.926 | 16.437 | 5000 | 3112 | NO | 19.45 | 0 | 0 | 0 | 112.81 | 676.86 | AT11 | A
AT | AT125 | ATAG_3-728 | ATTP_3-728 | ARA GAV Gmoosbach | 48.5995 | 16.086 | 14240 | 7648 | NO | 47.8 | 0 | 0 | 0 | 277.24 | 1663.44 | AT12 | C
AT | AT127 | ATAG_3-92 | ATTP_3-92 | ARA AV Raum Hainburg | 48.1444 | 16.9277 | 15000 | 9160 | NO | 57.25 | 0 | 0 | 0 | 332.05 | 1992.3 | AT12 | A
AT | AT124 | ATAG_3-848 | ATTP_3-848 | ARA GAV Eggenburg - Röschitz | 48.6589 | 15.9045 | 15000 | 13503 | NO | 84.3937 | 0 | 0 | 0 | 489.4837 | 2936.9025 | AT12 | C
AT | AT126 | ATAG_3-106 | ATTP_3-106 | ARA GAV Wagram - West | 48.3995 | 15.8004 | 15000 | 11863 | NO | 74.1437 | 0 | 0 | 0 | 430.0337 | 2580.2025 | AT12 | B
AT | AT127 | ATAG_3-398 | ATTP_3-398 | ARA Gumpoldskirchen | 48.0346 | 16.2933 | 15000 | 8128 | NO | 50.8 | 0 | 0 | 0 | 294.64 | 1767.84 | AT12 | A
AT | AT121 | ATAG_3-187 | ATTP_3-187 | ARA St. Valentin | 48.1806 | 14.537 | 15000 | 9231 | YES | 57.6938 | 184.62 | 138.465 | 276.93 | 334.6238 | 2007.7425 | AT12 | B
AT | AT123 | ATAG_3-145 | ATTP_3-145 | ARA AV Oberes Perschlingtal | 48.2384 | 15.7559 | 15300 | 12596 | NO | 78.725 | 0 | 0 | 0 | 456.605 | 2739.63 | AT12 | C
AT | AT122 | ATAG_3-713 | ATTP_3-713 | ARA GAV Aspang - Feistritz | 47.593 | 16.1105 | 16000 | 8664 | NO | 54.15 | 0 | 0 | 0 | 314.07 | 1884.42 | AT12 | C
AT | AT124 | ATAG_3-1127 | ATTP_3-1127 | ARA Abwasserreinigung im Waldviertel GmbH | 48.8196 | 15.2961 | 16700 | 9597 | NO | 59.9812 | 0 | 0 | 0 | 347.8913 | 2087.3475 | AT12 | A
AT | AT121 | ATAG_3-7 | ATTP_3-7 | ARA GV Abwasserreinigung im südlichen Waldviertel | 48.2191 | 15.2346 | 16800 | 6753 | NO | 42.2063 | 0 | 0 | 0 | 244.7963 | 1468.7775 | AT12 | A
AT | AT126 | ATAG_3-810 | ATTP_3-810 | ARA GAV Wagram - Nördliches Tullnerfeld | 48.3807 | 15.8804 | 17000 | 11225 | NO | 70.1562 | 0 | 0 | 0 | 406.9062 | 2441.4375 | AT12 | C
AT | AT122 | ATAG_3-369 | ATTP_3-369 | ARA AV Gölsental | 48.0528 | 15.6327 | 18000 | 19121 | NO | 119.5063 | 0 | 0 | 0 | 693.1363 | 4158.8175 | AT12 | A
AT | AT121 | ATAG_3-124 | ATTP_3-124 | ARA GAV Oberes Urltal | 48.0581 | 14.7055 | 18000 | 13950 | YES | 87.1875 | 279 | 209.25 | 418.5 | 505.6875 | 3034.125 | AT12 | C
AT | AT121 | ATAG_3-425 | ATTP_3-425 | ARA GAV Erlauftal | 48.0884 | 15.1435 | 19000 | 12142 | NO | 75.8875 | 0 | 0 | 0 | 440.1475 | 2640.885 | AT12 | C
AT | AT125 | ATAG_3-159 | ATTP_3-159 | ARA Poysdorf | 48.6522 | 16.6865 | 19800 | 8191 | NO | 51.1938 | 0 | 0 | 0 | 296.9237 | 1781.5425 | AT12 | B
AT | AT121 | ATAG_3-6 | ATTP_3-6 | ARA AV Ybbsfeld | 48.1691 | 15.0913 | 20000 | 19860 | NO | 124.125 | 0 | 0 | 0 | 719.925 | 4319.55 | AT12 | A
AT | AT126 | ATAG_3-105 | ATTP_3-105 | ARA GAV Raum St. Andrä-Wördern | 48.3408 | 16.216 | 20000 | 6413 | NO | 40.0813 | 0 | 0 | 0 | 232.4712 | 1394.8275 | AT12 | A
AT | AT127 | ATAG_3-49 | ATTP_3-49 | ARA Himberg | 48.0917 | 16.4403 | 20000 | 7884 | NO | 49.275 | 0 | 0 | 0 | 285.795 | 1714.77 | AT12 | A
AT | AT127 | ATAG_3-404 | ATTP_3-404 | ARA Vösendorf | 48.1176 | 16.3591 | 20000 | 13971 | NO | 87.3188 | 0 | 0 | 0 | 506.4488 | 3038.6925 | AT12 | B
AT | AT127 | ATAG_3-36 | ATTP_3-36 | ARA Ebreichsdorf | 47.9723 | 16.4138 | 20000 | 9740 | NO | 60.875 | 0 | 0 | 0 | 353.075 | 2118.45 | AT12 | A
AT | AT125 | ATAG_3-1050 | ATTP_3-1050 | ARA GAV Laaer Becken | 48.7315 | 16.3915 | 20800 | 15251 | NO | 95.3188 | 0 | 0 | 0 | 552.8487 | 3317.0925 | AT12 | A
AT | AT126 | ATAG_3-55 | ATTP_3-55 | ARA Wiental - Sammelkanal GmbH | 48.185 | 16.123 | 23000 | 17008 | YES | 106.3 | 340.16 | 255.12 | 510.24 | 616.54 | 3699.24 | AT12 | A
AT | AT121 | ATAG_3-51 | ATTP_3-51 | ARA GV Abwasserbeseitigung Raum Pöchlarn | 48.2148 | 15.2625 | 25000 | 13460 | YES | 84.125 | 269.2 | 201.9 | 403.8 | 487.925 | 2927.55 | AT12 | C
AT | AT125 | ATAG_3-764 | ATTP_3-764 | ARA Mistelbach | 48.5704 | 16.6105 | 25000 | 16341 | NO | 102.1313 | 0 | 0 | 0 | 592.3613 | 3554.1675 | AT12 | C
AT | AT127 | ATAG_3-1022 | ATTP_3-1022 | ARA Guntramsdorf | 48.042 | 16.3332 | 27000 | 14732 | NO | 92.075 | 0 | 0 | 0 | 534.035 | 3204.21 | AT12 | B
AT | AT125 | ATAG_3-10 | ATTP_3-10 | ARA Hollabrunn | 48.5484 | 16.073 | 30000 | 16810 | YES | 105.0625 | 336.2 | 252.15 | 504.3 | 609.3625 | 3656.175 | AT12 | A
AT | AT126 | ATAG_3-150 | ATTP_3-150 | ARA Stockerau | 48.3842 | 16.2297 | 30000 | 20196 | YES | 126.225 | 403.92 | 302.94 | 605.88 | 732.105 | 4392.63 | AT12 | A
AT | AT121 | ATAG_3-130 | ATTP_3-130 | ARA Waidhofen an der Ybbs | 47.9715 | 14.7596 | 31000 | 9810 | YES | 61.3125 | 196.2 | 147.15 | 294.3 | 355.6125 | 2133.675 | AT12 | A
AT | AT122 | ATAG_3-450 | ATTP_3-450 | ARA GV Abwasserbeseitigung Raum Hohe Wand - Steinfeld | 47.8229 | 16.1843 | 32000 | 13312 | NO | 83.2 | 0 | 0 | 0 | 482.56 | 2895.36 | AT12 | B
AT | AT127 | ATAG_3-38 | ATTP_3-38 | ARA Traiskirchen | 48.0311 | 16.3095 | 33000 | 19325 | NO | 120.7812 | 0 | 0 | 0 | 700.5312 | 4203.1875 | AT12 | A
AT | AT125 | ATAG_3-347 | ATTP_3-347 | ARA GAV Haugsdorf-Pernersdorf | 48.7059 | 16.0858 | 12000 | 1207 | NO | 7.5438 | 0 | 0 | 0 | 43.7537 | 262.5225 | AT12 | B
AT | AT127 | ATAG_3-396 | ATTP_3-396 | ARA AV Breitenfurt - Laab | 48.1365 | 16.2113 | 12000 | 5082 | NO | 31.7625 | 0 | 0 | 0 | 184.2225 | 1105.335 | AT12 | A
AT | AT126 | ATAG_3-121 | ATTP_3-121 | ARA Deutsch-Wagram | 48.2932 | 16.5575 | 12000 | 13379 | NO | 83.6188 | 0 | 0 | 0 | 484.9887 | 2909.9325 | AT12 | A
AT | AT126 | ATAG_3-772 | ATTP_3-772 | ARA GAV Oberer Weidenbach | 48.4381 | 16.6069 | 13000 | 5547 | NO | 34.6688 | 0 | 0 | 0 | 201.0788 | 1206.4725 | AT12 | C
AT | AT125 | ATAG_3-81 | ATTP_3-81 | ARA Retz | 48.7545 | 15.9657 | 13477 | 9369 | NO | 58.5563 | 0 | 0 | 0 | 339.6263 | 2037.7575 | AT12 | A
AT | AT126 | ATAG_3-152 | ATTP_3-152 | ARA GAV Mittleres Rußbachtal | 48.3941 | 16.4989 | 13500 | 6507 | NO | 40.6688 | 0 | 0 | 0 | 235.8787 | 1415.2725 | AT12 | B
AT | AT126 | ATAG_3-729 | ATTP_3-729 | ARA GAV Mittlerer Weidenbach | 48.3647 | 16.7121 | 14000 | 7322 | NO | 45.7625 | 0 | 0 | 0 | 265.4225 | 1592.535 | AT12 | B
AT | AT126 | ATAG_3-731 | ATTP_3-731 | ARA GAV Mittleres Schmidatal | 48.4422 | 15.9904 | 14000 | 7564 | NO | 47.275 | 0 | 0 | 0 | 274.195 | 1645.17 | AT12 | B
AT | AT127 | ATAG_3-25 | ATTP_3-25 | ARA GAV Ebenfurth-Pottendorf | 47.9111 | 16.4011 | 8500 | 12038 | NO | 75.2375 | 0 | 0 | 0 | 436.3775 | 2618.265 | AT12 | A
AT | AT126 | ATAG_3-707 | ATTP_3-707 | ARA Angern an der March | 48.363 | 16.8314 | 8500 | 2393 | NO | 14.9562 | 0 | 0 | 0 | 86.7462 | 520.4775 | AT12 | C
AT | AT126 | ATAG_3-828 | ATTP_3-828 | ARA GAV Sierndorf - Göllersdorf | 48.4203 | 16.1678 | 9000 | 10712 | NO | 66.95 | 0 | 0 | 0 | 388.31 | 2329.86 | AT12 | A
AT | AT125 | ATAG_3-244 | ATTP_3-244 | ARA GAV Unteres Zayatal | 48.5898 | 16.8315 | 9000 | 5730 | NO | 35.8125 | 0 | 0 | 0 | 207.7125 | 1246.275 | AT12 | B
AT | AT125 | ATAG_3-72 | ATTP_3-72 | ARA Zistersdorf | 48.5472 | 16.7804 | 9000 | 5487 | NO | 34.2938 | 0 | 0 | 0 | 198.9038 | 1193.4225 | AT12 | A
AT | AT127 | ATAG_3-2 | ATTP_3-2 | ARA GAV Fischatal | 48.0244 | 16.5009 | 9200 | 3809 | NO | 23.8063 | 0 | 0 | 0 | 138.0762 | 828.4575 | AT12 | A
AT | AT125 | ATAG_3-255 | ATTP_3-255 | ARA Sitzendorf an der Schmida | 48.5681 | 15.9321 | 9200 | 6047 | NO | 37.7938 | 0 | 0 | 0 | 219.2038 | 1315.2225 | AT12 | A
AT | AT341 | ATAG_8-Damuels | ATTP_8-Damuels | Damüls | 47.2807 | 9.8948 | 5000 | 2871 | NO | 17.9438 | 0 | 0 | 0 | 104.0738 | 624.4425 | AT34 | B
AT | AT341 | ATAG_8-Warth | ATTP_8-Warth | Warth | 47.2605 | 10.19 | 5000 | 1770 | NO | 11.0625 | 0 | 0 | 0 | 64.1625 | 384.975 | AT33 | C
AT | AT341 | ATAG_8-Boedmen | ATTP_8-Boedmen | Bödmen | 47.3156 | 10.1522 | 6225 | 2731 | YES | 17.0688 | 54.62 | 40.965 | 81.93 | 98.9988 | 593.9925 | AT34 | B
AT | AT342 | ATAG_8-Alberschwende | ATTP_8-Alberschwende | Alberschwende | 47.4491 | 9.8117 | 9200 | 3482 | NO | 21.7625 | 0 | 0 | 0 | 126.2225 | 757.335 | AT34 | A
AT | AT342 | ATAG_8-Rotachtal | ATTP_8-Rotachtal | Rotachtal | 47.5143 | 9.8616 | 16400 | 9044 | NO | 56.525 | 0 | 0 | 0 | 327.845 | 1967.07 | AT34 | C
AT | AT341 | ATAG_8-Riezlern | ATTP_8-Riezlern | Riezlern | 47.3582 | 10.1804 | 22200 | 8550 | YES | 53.4375 | 171 | 128.25 | 256.5 | 309.9375 | 1859.625 | AT34 | A
AT | AT342 | ATAG_8-Vorderland | ATTP_8-Vorderland | Vorderland | 47.3087 | 9.6174 | 27000 | 16471 | YES | 102.9438 | 329.42 | 247.065 | 494.13 | 597.0738 | 3582.4425 | AT34 | A
AT | AT125 | ATAG_3-733 | ATTP_3-733 | ARA GAV Taschlbach | 48.5403 | 16.5104 | 14000 | 4054 | NO | 25.3375 | 0 | 0 | 0 | 146.9575 | 881.745 | AT12 | B
AT | AT126 | ATAG_3-77 | ATTP_3-77 | ARA Gänserndorf | 48.3468 | 16.735 | 14000 | 9132 | NO | 57.075 | 0 | 0 | 0 | 331.035 | 1986.21 | AT12 | A
AT | AT121 | ATAG_3-3 | ATTP_3-3 | ARA Melk | 48.235 | 15.335 | 14000 | 6205 | YES | 38.7812 | 124.1 | 93.075 | 186.15 | 224.9312 | 1349.5875 | AT12 | B
AT | AT126 | ATAG_3-120 | ATTP_3-120 | ARA GAV Wolkersdorf - Pillichsdorf - Großengersdorf | 48.3581 | 16.5579 | 35000 | 19811 | NO | 123.8188 | 0 | 0 | 0 | 718.1488 | 4308.8925 | AT12 | A
AT | AT126 | ATAG_3-430 | ATTP_3-430 | ARA Tulln | 48.3339 | 16.0734 | 37000 | 29585 | YES | 184.9062 | 591.7 | 443.775 | 887.55 | 1072.4562 | 6434.7375 | AT12 | B
AT | AT122 | ATAG_3-182 | ATTP_3-182 | ARA AV Oberes Schwarzatal | 47.6753 | 15.9608 | 40000 | 25420 | YES | 158.875 | 508.4 | 381.3 | 762.6 | 921.475 | 5528.85 | AT12 | A
AT | AT126 | ATAG_3-132 | ATTP_3-132 | ARA AV Raum Korneuburg | 48.3324 | 16.332 | 40000 | 37259 | YES | 232.8688 | 745.18 | 558.885 | 1117.77 | 1350.6388 | 8103.8325 | AT12 | A
AT | AT127 | ATAG_3-43 | ATTP_3-43 | ARA GAV Trumau-Schönau | 48.0055 | 16.3542 | 40000 | 27623 | NO | 172.6437 | 0 | 0 | 0 | 1001.3337 | 6008.0025 | AT12 | A
AT | AT122 | ATAG_3-448 | ATTP_3-448 | ARA Piestingtaler AV | 47.9049 | 16.2624 | 60000 | 45395 | NO | 283.7188 | 0 | 0 | 0 | 1645.5687 | 9873.4125 | AT12 | B
AT | AT121 | ATAG_3-108 | ATTP_3-108 | ARA GAV Wieselburg | 48.1383 | 15.1534 | 64500 | 25461 | YES | 159.1312 | 509.22 | 381.915 | 763.83 | 922.9612 | 5537.7675 | AT12 | A
AT | AT124 | ATAG_3-851 | ATTP_3-851 | ARA GAV Langenlois - Schönberg am Kamp | 48.4693 | 15.7022 | 70000 | 35759 | NO | 223.4938 | 0 | 0 | 0 | 1296.2638 | 7777.5825 | AT12 | A
AT | AT127 | ATAG_3-34 | ATTP_3-34 | ARA GV Abwasserbeseitigung Raum Bad Vöslau | 47.969 | 16.2424 | 105000 | 90558 | YES | 565.9875 | 1811.16 | 1358.37 | 2716.74 | 3282.7275 | 19696.365 | AT12 | A
AT | AT122 | ATAG_3-447 | ATTP_3-447 | ARA AV Oberes Piestingtal | 47.8909 | 15.984 | 109683 | 40092 | YES | 250.575 | 801.84 | 601.38 | 1202.76 | 1453.335 | 8720.01 | AT12 | A
AT | AT127 | ATAG_3-403 | ATTP_3-403 | ARA Mödling | 48.0962 | 16.3302 | 130000 | 63708 | NO | 398.175 | 0 | 0 | 0 | 2309.415 | 13856.49 | AT12 | B
AT | AT127 | ATAG_3-643 | ATTP_3-643 | ARA AV Großraum Bruck an der Leitha - Neusiedl am See | 48.0308 | 16.8261 | 140500 | 82598 | YES | 516.2375 | 1651.96 | 1238.97 | 2477.94 | 2994.1775 | 17965.065 | AT12 | C
AT | AT126 | ATAG_3-142 | ATTP_3-142 | ARA Groß-Enzersdorf | 48.1788 | 16.5466 | 144000 | 130283 | YES | 814.2688 | 2605.66 | 1954.245 | 3908.49 | 4722.7587 | 28336.5525 | AT12 | B
AT | AT121 | ATAG_3-104 | ATTP_3-104 | ARA GAV Amstetten | 48.1086 | 14.8963 | 150000 | 139070 | YES | 869.1875 | 2781.4 | 2086.05 | 4172.1 | 5041.2875 | 30247.725 | AT12 | B
AT | AT124 | ATAG_3-119 | ATTP_3-119 | ARA GAV Raum Krems an der Donau | 48.4007 | 15.6629 | 255000 | 109717 | YES | 685.7312 | 2194.34 | 1645.755 | 3291.51 | 3977.2412 | 23863.4475 | AT12 | A
AT | AT122 | ATAG_3-449 | ATTP_3-449 | ARA AWV Wr. Neustadt-Süd | 47.8335 | 16.2756 | 260000 | 201059 | YES | 1256.6188 | 4021.18 | 3015.885 | 6031.77 | 7288.3888 | 43730.3325 | AT12 | A
AT | AT123 | ATAG_3-47 | ATTP_3-47 | ARA AV An der Traisen | 48.3632 | 15.7644 | 280000 | 225115 | YES | 1406.9688 | 4502.3 | 3376.725 | 6753.45 | 8160.4187 | 48962.5125 | AT12 | C
AT | AT127 | ATAG_3-11 | ATTP_3-11 | ARA AWV Schwechat | 48.1346 | 16.5412 | 370000 | 162228 | YES | 1013.925 | 3244.56 | 2433.42 | 4866.84 | 5880.765 | 35284.59 | AT12 | C
AT | AT126 | ATAG_3-433 | ATTP_3-433 | ARA GAV Südöstliches Tullnerfeld | 48.2904 | 15.9993 | 34000 | 42798 | YES | 267.4875 | 855.96 | 641.97 | 1283.94 | 1551.4275 | 9308.565 | AT12 | B
AT | AT123 | ATAG_3-162 | ATTP_3-162 | ARA AV Pielachtal | 48.2119 | 15.4984 | 35000 | 49351 | YES | 308.4438 | 987.02 | 740.265 | 1480.53 | 1788.9738 | 10733.8425 | AT12 | C
AT | AT113 | ATAG_1-00000055 | ATTP_1-00000055 | Rechnitz | 47.3015 | 16.4534 | 6000 | 3884 | NO | 24.275 | 0 | 0 | 0 | 140.795 | 844.77 | AT11 | A
AT | AT113 | ATAG_1-00000103 | ATTP_1-00000103 | Burg (Tauchental) | 47.2046 | 16.4132 | 7000 | 3179 | NO | 19.8688 | 0 | 0 | 0 | 115.2388 | 691.4325 | AT11 | C
AT | AT112 | ATAG_1-00000112 | ATTP_1-00000112 | Halbturn | 47.8558 | 17.001 | 7000 | 1894 | NO | 11.8375 | 0 | 0 | 0 | 68.6575 | 411.945 | AT11 | C
AT | AT112 | ATAG_1-00000013 | ATTP_1-00000013 | Frauenkirchen | 47.8269 | 16.9226 | 7250 | 3911 | NO | 24.4437 | 0 | 0 | 0 | 141.7737 | 850.6425 | AT11 | B
AT | AT112 | ATAG_1-00000001 | ATTP_1-00000001 | Andau | 47.7787 | 17.0491 | 8000 | 4201 | NO | 26.2562 | 0 | 0 | 0 | 152.2862 | 913.7175 | AT11 | B
AT | AT112 | ATAG_1-00000027 | ATTP_1-00000027 | Jois | 47.9491 | 16.7938 | 8400 | 5481 | NO | 34.2563 | 0 | 0 | 0 | 198.6862 | 1192.1175 | AT11 | B
AT | AT124 | ATAG_3-330 | ATTP_3-330 | ARA GV Horn für Abwasserbeseitigung | 48.6615 | 15.6669 | 40000 | 19411 | YES | 121.3188 | 388.22 | 291.165 | 582.33 | 703.6487 | 4221.8925 | AT12 | B
AT | AT124 | ATAG_3-458 | ATTP_3-458 | ARA Zwettl | 48.6127 | 15.1846 | 40000 | 21350 | YES | 133.4375 | 427 | 320.25 | 640.5 | 773.9375 | 4643.625 | AT12 | C
AT | AT122 | ATAG_3-421 | ATTP_3-421 | ARA AV Mittleres Schwarzatal | 47.7185 | 16.0468 | 41000 | 31620 | NO | 197.625 | 0 | 0 | 0 | 1146.225 | 6877.35 | AT12 | A
AT | AT126 | ATAG_3-134 | ATTP_3-134 | ARA GAV Marchfeld | 48.2591 | 16.653 | 42000 | 23535 | NO | 147.0938 | 0 | 0 | 0 | 853.1437 | 5118.8625 | AT12 | C
AT | AT127 | ATAG_3-29 | ATTP_3-29 | ARA Baden | 47.9947 | 16.264 | 45000 | 30598 | YES | 191.2375 | 611.96 | 458.97 | 917.94 | 1109.1775 | 6655.065 | AT12 | A
AT | AT123 | ATAG_3-52 | ATTP_3-52 | ARA AV Anzbach-Laabental | 48.223 | 15.9212 | 47000 | 33254 | YES | 207.8375 | 665.08 | 498.81 | 997.62 | 1205.4575 | 7232.745 | AT12 | A
AT | AT124 | ATAG_3-757 | ATTP_3-757 | ARA AV Lainsitz | 48.7956 | 14.9574 | 50000 | 26859 | YES | 167.8688 | 537.18 | 402.885 | 805.77 | 973.6387 | 5841.8325 | AT12 | C
AT | AT126 | ATAG_3-32 | ATTP_3-32 | ARA Klosterneuburg | 48.2942 | 16.34 | 55000 | 32281 | YES | 201.7563 | 645.62 | 484.215 | 968.43 | 1170.1862 | 7021.1175 | AT12 | A
AT | AT113 | ATAG_1-00000097 | ATTP_1-00000097 | Neumarkt (Tauchental) | 47.2841 | 16.2981 | 10000 | 6939 | NO | 43.3687 | 0 | 0 | 0 | 251.5387 | 1509.2325 | AT11 | C
AT | AT113 | ATAG_1-00000064 | ATTP_1-00000064 | Bocksdorf (Oberes Stremtal) | 47.1382 | 16.1831 | 12500 | 28085 | NO | 175.5312 | 0 | 0 | 0 | 1018.0812 | 6108.4875 | AT11 | B
AT | AT112 | ATAG_1-00000078 | ATTP_1-00000078 | Nickelsdorf (Nickelsdorf - Zurndorf) | 47.9448 | 17.0894 | 12500 | 6035 | NO | 37.7188 | 0 | 0 | 0 | 218.7687 | 1312.6125 | AT11 | C
AT | AT113 | ATAG_1-00000081 | ATTP_1-00000081 | Wolfau (Stögersbachtal) | 47.2535 | 16.0918 | 14500 | 11207 | NO | 70.0438 | 0 | 0 | 0 | 406.2537 | 2437.5225 | AT11 | B
AT | AT111 | ATAG_1-00000030 | ATTP_1-00000030 | Klostermarienberg (Lockenhaus) Günstal | 47.4243 | 16.5804 | 15200 | 12078 | NO | 75.4875 | 0 | 0 | 0 | 437.8275 | 2626.965 | AT11 | C
AT | AT112 | ATAG_1-00000051 | ATTP_1-00000051 | Podersdorf | 47.8637 | 16.8392 | 20000 | 3181 | NO | 19.8813 | 0 | 0 | 0 | 115.3113 | 691.8675 | AT11 | A
AT | AT111 | ATAG_1-00000044 | ATTP_1-00000044 | Oberpullendorf (Mittleres Burgenland) Stooberbachtal | 47.4888 | 16.5274 | 25000 | 20089 | YES | 125.5562 | 401.78 | 301.335 | 602.67 | 728.2262 | 4369.3575 | AT11 | A
AT | AT113 | ATAG_1-00000050 | ATTP_1-00000050 | Riedlingsdorf (Oberes Pinkatal) | 47.3287 | 16.1486 | 25500 | 15577 | NO | 97.3563 | 0 | 0 | 0 | 564.6662 | 3387.9975 | AT11 | C
AT | AT112 | ATAG_1-00000077 | ATTP_1-00000077 | Pamhagen (Seewinkel) | 47.7204 | 16.8732 | 26300 | 18560 | NO | 116 | 0 | 0 | 0 | 672.8 | 4036.8 | AT11 | C
AT | AT122 | ATAG_1-00000040 | ATTP_1-00000040 | Neufeld (Neufelderseengebiet) | 47.8816 | 16.3838 | 28700 | 15942 | NO | 99.6375 | 0 | 0 | 0 | 577.8975 | 3467.385 | AT12 | B
AT | AT113 | ATAG_1-00000079 | ATTP_1-00000079 | Glasing (Mittleres Strem- und Zickenbachtal) | 47.0478 | 16.3651 | 35000 | 25790 | NO | 161.1875 | 0 | 0 | 0 | 934.8875 | 5609.325 | AT11 | C
AT | AT112 | ATAG_1-00000016 | ATTP_1-00000016 | Gols (Gols - Mönchhof) | 47.8857 | 16.92 | 40000 | 17734 | NO | 110.8375 | 0 | 0 | 0 | 642.8575 | 3857.145 | AT11 | A
AT | AT113 | ATAG_1-00000057 | ATTP_1-00000057 | Siget / Wart (Mittleres Pinka- und Zickenbachtal) | 47.2537 | 16.2784 | 45000 | 52420 | YES | 327.625 | 1048.4 | 786.3 | 1572.6 | 1900.225 | 11401.35 | AT11 | B
AT | AT112 | ATAG_1-00000010 | ATTP_1-00000010 | Eisenstadt (Eisbachtal) | 47.8311 | 16.5422 | 54000 | 33107 | NO | 206.9188 | 0 | 0 | 0 | 1200.1288 | 7200.7725 | AT11 | A
AT | AT111 | ATAG_1-00000005 | ATTP_1-00000005 | Deutschkreuz (Mittleres Burgenland) Goldbachtal | 47.5945 | 16.6406 | 65000 | 16679 | NO | 104.2437 | 0 | 0 | 0 | 604.6137 | 3627.6825 | AT11 | A
AT | AT112 | ATAG_1-00000145 | ATTP_1-00000145 | Schützen (Neusiedlersee-Westufer) | 47.8581 | 16.6482 | 66500 | 21095 | NO | 131.8438 | 0 | 0 | 0 | 764.6938 | 4588.1625 | AT11 | C
AT | AT112 | ATAG_1-00000074 | ATTP_1-00000074 | Wulkaprodersdorf (Wulkatal) | 47.8006 | 16.5173 | 110000 | 73447 | NO | 459.0438 | 0 | 0 | 0 | 2662.4538 | 15974.7225 | AT11 | B
AT | AT113 | ATAG_1-00000133 | ATTP_1-00000133 | Heiligenkreuz/Lafnitztal (Bez.Jennersdorf) Lafnitztal-Raabtal | 46.9659 | 16.2582 | 130000 | 45970 | YES | 287.3125 | 919.4 | 689.55 | 1379.1 | 1666.4125 | 9998.475 | AT11 | A
AT | AT211 | ATAG_2-K1843518R0 | ATTP_2-K1843518R0 | ABUG-Abwasserbeseitigung Unteres Gailtal Errichtungs- und Betriebsgesellschaft | 46.5813 | 13.6193 | 6425 | 3870 | NO | 24.1875 | 0 | 0 | 0 | 140.2875 | 841.725 | AT21 | A
AT | AT211 | ATAG_2-K1933909 | ATTP_2-K1933909 | Gemeinde Poggersdorf | 46.6421 | 14.4265 | 6500 | 4708 | NO | 29.425 | 0 | 0 | 0 | 170.665 | 1023.99 | AT21 | B
AT | AT212 | ATAG_2-K1543752R0 | ATTP_2-K1543752R0 | ABKM ABKM-Abwasserbeseitigung Kötschach-Mauthen Errichtung und Betriebsgesellschaft | 46.6699 | 13.0154 | 7000 | 4904 | NO | 30.65 | 0 | 0 | 0 | 177.77 | 1066.62 | AT21 | B
AT | AT211 | ATAG_2-K1669675R0 | ATTP_2-K1669675R0 | Gemeinde Ferndorf | 46.7231 | 13.6388 | 7000 | 4814 | NO | 30.0875 | 0 | 0 | 0 | 174.5075 | 1047.045 | AT21 | B
AT | AT212 | ATAG_2-K2391503 | ATTP_2-K2391503 | Gemeinde Dellach/Gemeinde Berg | 46.7383 | 13.0994 | 7800 | 4366 | NO | 27.2875 | 0 | 0 | 0 | 158.2675 | 949.605 | AT21 | B
AT | AT213 | ATAG_2-K1702958R0 | ATTP_2-K1702958R0 | Abwasserverband "Oberes Lavanttal" | 46.9328 | 14.8292 | 8000 | 7767 | NO | 48.5437 | 0 | 0 | 0 | 281.5537 | 1689.3225 | AT21 | A
AT | AT212 | ATAG_2-K1639918R0 | ATTP_2-K1639918R0 | Gemeinde Heiligenblut | 47.0154 | 12.8667 | 8250 | 1741 | NO | 10.8812 | 0 | 0 | 0 | 63.1112 | 378.6675 | AT21 | C
AT | AT213 | ATAG_2-K2307771 | ATTP_2-K2307771 | WV Abwasserverband Görtschitztal | 46.7382 | 14.5334 | 9000 | 7854 | NO | 49.0875 | 0 | 0 | 0 | 284.7075 | 1708.245 | AT21 | A
AT | AT211 | ATAG_2-K1950736 | ATTP_2-K1950736 | Stadtgemeinde Ferlach | 46.5425 | 14.3046 | 10000 | 8546 | NO | 53.4125 | 0 | 0 | 0 | 309.7925 | 1858.755 | AT21 | B
AT | AT213 | ATAG_2-K1610676R0 | ATTP_2-K1610676R0 | Reinhalteverband für das Gebiet St. Veit/Glan | 46.74 | 14.3853 | 65000 | 58477 | NO | 365.4813 | 0 | 0 | 0 | 2119.7913 | 12718.7475 | AT21 | C
AT | AT213 | ATAG_2-K1702940R0 | ATTP_2-K1702940R0 | Reinhalteverband "Mittleres Lavanttal" | 46.7368 | 14.846 | 120000 | 111264 | NO | 695.4 | 0 | 0 | 0 | 4033.32 | 24199.92 | AT21 | C
AT | AT212 | ATAG_2-K1949374 | ATTP_2-K1949374 | WV Millstätter See | 46.7796 | 13.519 | 130000 | 94745 | YES | 592.1562 | 1894.9 | 1421.175 | 2842.35 | 3434.5062 | 20607.0375 | AT21 | B
AT | AT211 | ATAG_2-K1939997 | ATTP_2-K1939997 | Stadtgemeinde Villach | 46.612 | 13.8771 | 200000 | 149490 | YES | 934.3125 | 2989.8 | 2242.35 | 4484.7 | 5419.0125 | 32514.075 | AT21 | B
AT | AT211 | ATAG_2-K1931629 | ATTP_2-K1931629 | Wasserverband Wörthersee Ost | 46.6061 | 14.3337 | 300000 | 219672 | NO | 1372.95 | 0 | 0 | 0 | 7963.11 | 47778.66 | AT21 | A
AT | AT125 | ATAG_3-154 | ATTP_3-154 | ARA Wildendürnbach | 48.7556 | 16.4877 | 5000 | 1187 | NO | 7.4188 | 0 | 0 | 0 | 43.0288 | 258.1725 | AT12 | A
AT | AT122 | ATAG_3-476 | ATTP_3-476 | ARA GV Altenmarkt an der Triesting - Kaumberg | 48.0108 | 16.0087 | 5000 | 1896 | NO | 11.85 | 0 | 0 | 0 | 68.73 | 412.38 | AT12 | A
AT | AT124 | ATAG_3-355 | ATTP_3-355 | ARA Hadersdorf | 48.4519 | 15.7194 | 5000 | 3069 | NO | 19.1813 | 0 | 0 | 0 | 111.2512 | 667.5075 | AT12 | B
AT | AT125 | ATAG_3-71 | ATTP_3-71 | ARA Hohenau an der March | 48.6062 | 16.9137 | 5000 | 3541 | NO | 22.1312 | 0 | 0 | 0 | 128.3612 | 770.1675 | AT12 | A
AT | AT121 | ATAG_3-45 | ATTP_3-45 | ARA Loosdorf | 48.2103 | 15.3905 | 5000 | 6192 | NO | 38.7 | 0 | 0 | 0 | 224.46 | 1346.76 | AT12 | A
AT | AT121 | ATAG_3-80 | ATTP_3-80 | ARA Lunz am See | 47.8553 | 15.021 | 5000 | 833 | NO | 5.2062 | 0 | 0 | 0 | 30.1962 | 181.1775 | AT12 | A
AT | AT121 | ATAG_3-176 | ATTP_3-176 | ARA Ybbsitz | 47.9405 | 14.8511 | 5000 | 3068 | NO | 19.175 | 0 | 0 | 0 | 111.215 | 667.29 | AT12 | C
AT | AT126 | ATAG_3-1041 | ATTP_3-1041 | ARA EVN Wasser (GAV Senningbach) | 48.4589 | 16.239 | 5000 | 2343 | NO | 14.6437 | 0 | 0 | 0 | 84.9337 | 509.6025 | AT12 | C
AT | AT121 | ATAG_3-46 | ATTP_3-46 | ARA Pöggstall | 48.3153 | 15.2139 | 5270 | 4786 | NO | 29.9125 | 0 | 0 | 0 | 173.4925 | 1040.955 | AT12 | B
AT | AT125 | ATAG_3-346 | ATTP_3-346 | ARA Zellerndorf | 48.6999 | 15.989 | 5400 | 3379 | NO | 21.1188 | 0 | 0 | 0 | 122.4887 | 734.9325 | AT12 | B
AT | AT121 | ATAG_3-1631 | ATTP_3-1610 | ARA Gaming | 47.9401 | 15.1265 | 5500 | 1826 | NO | 11.4125 | 0 | 0 | 0 | 66.1925 | 397.155 | AT12 | A
AT | AT124 | ATAG_3-88 | ATTP_3-88 | ARA AV Lainsitz-Mitte | 48.7063 | 14.8922 | 5800 | 4100 | NO | 25.625 | 0 | 0 | 0 | 148.625 | 891.75 | AT12 | A
AT | AT125 | ATAG_3-91 | ATTP_3-91 | ARA GAV Retzbach - Retz | 48.7413 | 16.03 | 5900 | 4671 | NO | 29.1937 | 0 | 0 | 0 | 169.3237 | 1015.9425 | AT12 | C
AT | AT125 | ATAG_3-345 | ATTP_3-345 | ARA Pulkau | 48.6998 | 15.881 | 5900 | 2192 | NO | 13.7 | 0 | 0 | 0 | 79.46 | 476.76 | AT12 | B
AT | AT126 | ATAG_3-301 | ATTP_3-301 | ARA AV Oberes Russbachtal | 48.4422 | 16.4263 | 6000 | 4148 | NO | 25.925 | 0 | 0 | 0 | 150.365 | 902.19 | AT12 | C
AT | AT126 | ATAG_3-221 | ATTP_3-221 | ARA AV Sulzbach | 48.4652 | 16.8082 | 6000 | 4667 | NO | 29.1688 | 0 | 0 | 0 | 169.1788 | 1015.0725 | AT12 | A
AT | AT126 | ATAG_3-166 | ATTP_3-166 | ARA GAV Kleinharraserbach | 48.4592 | 16.6227 | 6000 | 2054 | NO | 12.8375 | 0 | 0 | 0 | 74.4575 | 446.745 | AT12 | A
AT | AT124 | ATAG_3-850 | ATTP_3-850 | ARA GAV Maignerbach | 48.6768 | 15.8184 | 6000 | 951 | NO | 5.9438 | 0 | 0 | 0 | 34.4738 | 206.8425 | AT12 | B
AT | AT126 | ATAG_3-829 | ATTP_3-829 | ARA GAV Unteres Schmidatal | 48.3695 | 16.1075 | 6000 | 5245 | NO | 32.7812 | 0 | 0 | 0 | 190.1312 | 1140.7875 | AT12 | C
AT | AT125 | ATAG_3-683 | ATTP_3-683 | ARA Herrnbaumgarten | 48.6991 | 16.7033 | 6000 | 977 | NO | 6.1063 | 0 | 0 | 0 | 35.4162 | 212.4975 | AT12 | B
AT | AT126 | ATAG_3-814 | ATTP_3-814 | ARA Leopoldsdorf im Marchfelde | 48.2321 | 16.7082 | 6000 | 1915 | NO | 11.9688 | 0 | 0 | 0 | 69.4187 | 416.5125 | AT12 | A
AT | AT127 | ATAG_3-89 | ATTP_3-89 | ARA Sooß | 47.9834 | 16.2258 | 6000 | 616 | NO | 3.85 | 0 | 0 | 0 | 22.33 | 133.98 | AT12 | A
AT | AT124 | ATAG_3-1701 | ATTP_3-1701 | ARA Litschau | 48.9451 | 15.0424 | 6000 | 3264 | NO | 20.4 | 0 | 0 | 0 | 118.32 | 709.92 | AT12 | A
AT | AT122 | ATAG_3-812 | ATTP_3-812 | ARA WVG Bad Schönau - Krumbach | 47.5049 | 16.2398 | 6000 | 5267 | NO | 32.9188 | 0 | 0 | 0 | 190.9287 | 1145.5725 | AT12 | C
AT | AT122 | ATAG_3-730 | ATTP_3-730 | ARA GAV Mittleres Pittental | 47.6868 | 16.1302 | 6500 | 6733 | NO | 42.0813 | 0 | 0 | 0 | 244.0713 | 1464.4275 | AT12 | C
AT | AT124 | ATAG_3-137 | ATTP_3-137 | ARA Allentsteig | 48.7222 | 15.3275 | 6600 | 3039 | NO | 18.9938 | 0 | 0 | 0 | 110.1637 | 660.9825 | AT12 | B
AT | AT126 | ATAG_3-61 | ATTP_3-61 | ARA Gablitz | 48.2169 | 16.1639 | 7000 | 6440 | NO | 40.25 | 0 | 0 | 0 | 233.45 | 1400.7 | AT12 | A
AT | AT124 | ATAG_3-322 | ATTP_3-322 | ARA Gars am Kamp | 48.5902 | 15.6573 | 7000 | 7058 | NO | 44.1125 | 0 | 0 | 0 | 255.8525 | 1535.115 | AT12 | A
AT | AT121 | ATAG_3-701 | ATTP_3-701 | ARA Göstling | 47.8119 | 14.9298 | 7000 | 3650 | NO | 22.8125 | 0 | 0 | 0 | 132.3125 | 793.875 | AT12 | A
AT | AT127 | ATAG_3-402 | ATTP_3-402 | ARA Laxenburg | 48.0681 | 16.3675 | 7200 | 2868 | NO | 17.925 | 0 | 0 | 0 | 103.965 | 623.79 | AT12 | B
AT | AT125 | ATAG_3-705 | ATTP_3-705 | ARA GAV Drasenhofen | 48.7659 | 16.6592 | 7300 | 1375 | NO | 8.5938 | 0 | 0 | 0 | 49.8438 | 299.0625 | AT12 | C
AT | AT125 | ATAG_3-136 | ATTP_3-136 | ARA VG Ravelsbach - Maissau | 48.5536 | 15.8866 | 7372 | 4833 | NO | 30.2063 | 0 | 0 | 0 | 175.1962 | 1051.1775 | AT12 | C
AT | AT124 | ATAG_3-434 | ATTP_3-434 | ARA Groß-Siegharts | 48.7994 | 15.4179 | 7500 | 5955 | NO | 37.2188 | 0 | 0 | 0 | 215.8687 | 1295.2125 | AT12 | A
AT | AT121 | ATAG_3-477 | ATTP_3-477 | ARA GAV Ruprechtshofen - St. Leonhard am Forst | 48.1499 | 15.2597 | 8000 | 7160 | NO | 44.75 | 0 | 0 | 0 | 259.55 | 1557.3 | AT12 | C
AT | AT121 | ATAG_3-109 | ATTP_3-109 | ARA Haag | 48.1148 | 14.5456 | 8000 | 3212 | NO | 20.075 | 0 | 0 | 0 | 116.435 | 698.61 | AT12 | C
AT | AT125 | ATAG_3-99 | ATTP_3-99 | ARA GAV Raum Groß-Kadolz | 48.7099 | 16.1923 | 9860 | 4526 | NO | 28.2875 | 0 | 0 | 0 | 164.0675 | 984.405 | AT12 | A
AT | AT121 | ATAG_3-65 | ATTP_3-65 | ARA GAV Ennsdorf-St.Pantaleon | 48.2304 | 14.5361 | 10000 | 11676 | NO | 72.975 | 0 | 0 | 0 | 423.255 | 2539.53 | AT12 | B
AT | AT126 | ATAG_3-842 | ATTP_3-842 | ARA GAV Östliches Tullnerfeld | 48.3087 | 16.134 | 10000 | 4548 | NO | 28.425 | 0 | 0 | 0 | 164.865 | 989.19 | AT12 | C
AT | AT127 | ATAG_3-184 | ATTP_3-184 | ARA Alland | 48.0414 | 16.101 | 10000 | 5667 | NO | 35.4188 | 0 | 0 | 0 | 205.4287 | 1232.5725 | AT12 | C
AT | AT127 | ATAG_3-63 | ATTP_3-63 | ARA Seibersdorf | 47.9429 | 16.4943 | 10000 | 5110 | NO | 31.9375 | 0 | 0 | 0 | 185.2375 | 1111.425 | AT12 | B
AT | AT122 | ATAG_3-408 | ATTP_3-408 | ARA AV Grimmenstein-Edlitz-Thomasberg | 47.6284 | 16.1299 | 10270 | 10864 | NO | 67.9 | 0 | 0 | 0 | 393.82 | 2362.92 | AT12 | A
AT | AT121 | ATAG_3-424 | ATTP_3-424 | ARA GAV Kleines Erlauftal | 48.0707 | 15.0755 | 10500 | 5540 | NO | 34.625 | 0 | 0 | 0 | 200.825 | 1204.95 | AT12 | C
AT | AT125 | ATAG_3-127 | ATTP_3-127 | ARA Ziersdorf | 48.5284 | 15.9429 | 6000 | 5253 | NO | 32.8313 | 0 | 0 | 0 | 190.4213 | 1142.5275 | AT12 | B
AT | AT225 | ATAG_6-M3728231R0 | ATTP_6-M3728231R0 | Lebring-St.Margarethen | 46.844 | 15.5508 | 7000 | 3215 | NO | 20.0938 | 0 | 0 | 0 | 116.5438 | 699.2625 | AT22 | B
AT | AT224 | ATAG_6-M3586829R0 | ATTP_6-M3586829R0 | Vorau | 47.3981 | 15.9058 | 7000 | 3397 | NO | 21.2312 | 0 | 0 | 0 | 123.1412 | 738.8475 | AT22 | C
AT | AT224 | ATAG_6-M3283419R0 | ATTP_6-M3283419R0 | Bad Waltersdorf-Leitersdorf | 47.1485 | 16.0338 | 7000 | 6428 | NO | 40.175 | 0 | 0 | 0 | 233.015 | 1398.09 | AT22 | B
AT | AT222 | ATAG_6-M3318866R0 | ATTP_6-M3318866R0 | Altenmarkt bei St. Gallen | 47.7141 | 14.637 | 7500 | 3423 | NO | 21.3938 | 0 | 0 | 0 | 124.0837 | 744.5025 | AT22 | A
AT | AT224 | ATAG_6-M4321937 | ATTP_6-M4321937 | Birkfeld | 47.3505 | 15.6979 | 7500 | 4188 | NO | 26.175 | 0 | 0 | 0 | 151.815 | 910.89 | AT22 | A
AT | AT225 | ATAG_6-M3455849R0 | ATTP_6-M3455849R0 | Pitschgau-Eibiswald | 46.702 | 15.2943 | 7520 | 5424 | NO | 33.9 | 0 | 0 | 0 | 196.62 | 1179.72 | AT22 | B
AT | AT224 | ATAG_6-M3634931R0 | ATTP_6-M3634931R0 | Lafnitz-Rohrbach | 47.3561 | 16.0285 | 8000 | 6098 | NO | 38.1125 | 0 | 0 | 0 | 221.0525 | 1326.315 | AT22 | C
AT | AT224 | ATAG_6-M3292250R0 | ATTP_6-M3292250R0 | Unterfeistritz | 47.2397 | 15.7407 | 8000 | 5167 | NO | 32.2938 | 0 | 0 | 0 | 187.3037 | 1123.8225 | AT22 | C
AT | AT225 | ATAG_6-M3728315R0 | ATTP_6-M3728315R0 | Gralla | 46.8161 | 15.5802 | 8000 | 2883 | NO | 18.0188 | 0 | 0 | 0 | 104.5087 | 627.0525 | AT22 | B
AT | AT226 | ATAG_6-M3520257R0 | ATTP_6-M3520257R0 | Neumarkt | 47.0611 | 14.4313 | 8000 | 6358 | NO | 39.7375 | 0 | 0 | 0 | 230.4775 | 1382.865 | AT22 | A
AT | AT222 | ATAG_6-M3589961R0 | ATTP_6-M3589961R0 | Trieben | 47.4977 | 14.4707 | 8500 | 7989 | YES | 49.9313 | 159.78 | 119.835 | 239.67 | 289.6012 | 1737.6075 | AT22 | B
AT | AT222 | ATAG_6-M3670920R0 | ATTP_6-M3670920R0 | Gröbming-Ennsboden | 47.4364 | 13.92 | 9000 | 7482 | NO | 46.7625 | 0 | 0 | 0 | 271.2225 | 1627.335 | AT22 | C
AT | AT222 | ATAG_6-M3341478R0 | ATTP_6-M3341478R0 | Hall/Admont | 47.5809 | 14.4681 | 9000 | 4086 | YES | 25.5375 | 81.72 | 61.29 | 122.58 | 148.1175 | 888.705 | AT22 | B
AT | AT224 | ATAG_6-M3235303R0 | ATTP_6-M3235303R0 | Pöllau-VKA | 47.2851 | 15.8471 | 9000 | 7213 | NO | 45.0813 | 0 | 0 | 0 | 261.4712 | 1568.8275 | AT22 | C
AT | AT222 | ATAG_6-M3273368R0 | ATTP_6-M3273368R0 | Bad Mitterndorf | 47.5469 | 13.9218 | 9400 | 2048 | YES | 12.8 | 40.96 | 30.72 | 61.44 | 74.24 | 445.44 | AT22 | A
AT | AT225 | ATAG_6-M3230905R0 | ATTP_6-M3230905R0 | St.Johann im Saggautal | 46.7253 | 15.4132 | 10000 | 8074 | NO | 50.4625 | 0 | 0 | 0 | 292.6825 | 1756.095 | AT22 | C
AT | AT221 | ATAG_6-M3445287R0 | ATTP_6-M3445287R0 | Dobl-Muttendorf | 46.939 | 15.3712 | 10000 | 8670 | NO | 54.1875 | 0 | 0 | 0 | 314.2875 | 1885.725 | AT22 | B
AT | AT224 | ATAG_6-M3283441R0 | ATTP_6-M3283441R0 | Sebersdorf | 47.1824 | 16.0013 | 10000 | 4700 | NO | 29.375 | 0 | 0 | 0 | 170.375 | 1022.25 | AT22 | B
AT | AT223 | ATAG_6-M3616874R0 | ATTP_6-M3616874R0 | Mariazell | 47.7611 | 15.3067 | 11000 | 5373 | NO | 33.5813 | 0 | 0 | 0 | 194.7713 | 1168.6275 | AT22 | A
AT | AT222 | ATAG_6-M3336492R0 | ATTP_6-M3336492R0 | Rottenmann | 47.5311 | 14.3191 | 11000 | 6513 | YES | 40.7063 | 130.26 | 97.695 | 195.39 | 236.0962 | 1416.5775 | AT22 | C
AT | AT224 | ATAG_6-M3230038R0 | ATTP_6-M3230038R0 | Passail | 47.2579 | 15.5038 | 11000 | 7699 | NO | 48.1188 | 0 | 0 | 0 | 279.0888 | 1674.5325 | AT22 | C
AT | AT226 | ATAG_6-M3675325R0 | ATTP_6-M3675325R0 | Fohnsdorf | 47.1895 | 14.6887 | 11000 | 10423 | YES | 65.1437 | 208.46 | 156.345 | 312.69 | 377.8337 | 2267.0025 | AT22 | A
AT | AT224 | ATAG_6-M3680278R0 | ATTP_6-M3680278R0 | Fehring | 46.9438 | 16.0172 | 11000 | 8981 | NO | 56.1313 | 0 | 0 | 0 | 325.5613 | 1953.3675 | AT22 | B
AT | AT221 | ATAG_6-M3507571R0 | ATTP_6-M3507571R0 | Lieboch | 46.9639 | 15.3455 | 12000 | 8167 | NO | 51.0437 | 0 | 0 | 0 | 296.0537 | 1776.3225 | AT22 | A
AT | AT224 | ATAG_6-M3448019R0 | ATTP_6-M3448019R0 | Fladnitz im Raabtal | 46.9817 | 15.7989 | 12000 | 8027 | NO | 50.1687 | 0 | 0 | 0 | 290.9787 | 1745.8725 | AT22 | C
AT | AT223 | ATAG_6-M3410748R0 | ATTP_6-M3410748R0 | Eisenerz | 47.5663 | 14.8541 | 12000 | 9355 | NO | 58.4688 | 0 | 0 | 0 | 339.1187 | 2034.7125 | AT22 | A
AT | AT222 | ATAG_6-M3776783R0 | ATTP_6-M3776783R0 | Ramsau | 47.4197 | 13.6826 | 12550 | 6059 | NO | 37.8687 | 0 | 0 | 0 | 219.6387 | 1317.8325 | AT22 | B
AT | AT221 | ATAG_6-M3232571R0 | ATTP_6-M3232571R0 | Hitzendorf | 47.027 | 15.304 | 14000 | 13026 | NO | 81.4125 | 0 | 0 | 0 | 472.1925 | 2833.155 | AT22 | B
AT | AT222 | ATAG_6-M3327097R0 | ATTP_6-M3327097R0 | Pichl-Preunegg | 47.3957 | 13.5885 | 14000 | 7364 | NO | 46.025 | 0 | 0 | 0 | 266.945 | 1601.67 | AT22 | C
AT | AT222 | ATAG_6-M3226627R0 | ATTP_6-M3226627R0 | Liezen | 47.5569 | 14.2592 | 14000 | 15086 | YES | 94.2875 | 301.72 | 226.29 | 452.58 | 546.8675 | 3281.205 | AT22 | A
AT | AT224 | ATAG_6-M3343322R0 | ATTP_6-M3343322R0 | Bad Radkersburg | 46.6839 | 16.0058 | 16000 | 9468 | NO | 59.175 | 0 | 0 | 0 | 343.215 | 2059.29 | AT22 | B
AT | AT225 | ATAG_6-M3446308R0 | ATTP_6-M3446308R0 | Zehndorf | 46.8438 | 15.4177 | 17000 | 9005 | NO | 56.2812 | 0 | 0 | 0 | 326.4312 | 1958.5875 | AT22 | C
AT | AT314 | ATAG_4-40920002 | ATTP_4-40920002 | Mittleres Steyrtal | 47.9808 | 14.2752 | 5000 | 2223 | NO | 13.8937 | 0 | 0 | 0 | 80.5837 | 483.5025 | AT31 | A
AT | AT313 | ATAG_4-41312002 | ATTP_4-41312002 | Niederranna Hofkirchen | 48.4673 | 13.7982 | 5000 | 2553 | NO | 15.9562 | 0 | 0 | 0 | 92.5462 | 555.2775 | AT31 | C
AT | AT212 | ATAG_2-K2391520 | ATTP_2-K2391520 | Marktgemeinde Steinfeld und Greifenburg/Gemeinde Weißensee | 46.7548 | 13.2609 | 13300 | 8678 | NO | 54.2375 | 0 | 0 | 0 | 314.5775 | 1887.465 | AT21 | A
AT | AT212 | ATAG_2-K1620535R0 | ATTP_2-K1620535R0 | WV Reinhalteverband Mölltal | 46.9193 | 13.2165 | 15000 | 7716 | NO | 48.225 | 0 | 0 | 0 | 279.705 | 1678.23 | AT21 | C
AT | AT211 | ATAG_2-K1822227R0 | ATTP_2-K1822227R0 | Wasserverband Unteres Drautal | 46.6717 | 13.729 | 23000 | 10034 | NO | 62.7125 | 0 | 0 | 0 | 363.7325 | 2182.395 | AT21 | C
AT | AT213 | ATAG_2-K1750774R0 | ATTP_2-K1750774R0 | Gemeinde St. Kanzian am Klopeinersee | 46.6206 | 14.5863 | 25000 | 11667 | NO | 72.9188 | 0 | 0 | 0 | 422.9288 | 2537.5725 | AT21 | B
AT | AT213 | ATAG_2-K1610301R0 | ATTP_2-K1610301R0 | WV Abwasserverband Raum Friesach-Althofen | 46.8608 | 14.4558 | 32000 | 27844 | YES | 174.025 | 556.88 | 417.66 | 835.32 | 1009.345 | 6056.07 | AT21 | B
AT | AT212 | ATAG_2-K1949430 | ATTP_2-K1949430 | Abwasserverband Karnische Region | 46.6103 | 13.4911 | 44000 | 18465 | NO | 115.4062 | 0 | 0 | 0 | 669.3563 | 4016.1375 | AT21 | C
AT | AT211 | ATAG_2-K1944050 | ATTP_2-K1944050 | Abwasserverband Wörthersee West | 46.5732 | 14.024 | 44000 | 26354 | NO | 164.7125 | 0 | 0 | 0 | 955.3325 | 5731.995 | AT21 | C
AT | AT213 | ATAG_2-K1518811R0 | ATTP_2-K1518811R0 | WV Abwasserverband Völkermarkt-Jaunfeld (Eberndorf) | 46.6399 | 14.6538 | 46000 | 35642 | NO | 222.7625 | 0 | 0 | 0 | 1292.0225 | 7752.135 | AT21 | C
AT | AT212 | ATAG_2-K1939137 | ATTP_2-K1939137 | WV Ossiacher See | 46.7121 | 14.0817 | 50000 | 34850 | YES | 217.8125 | 697 | 522.75 | 1045.5 | 1263.3125 | 7579.875 | AT21 | A
AT | AT311 | ATAG_4-40818001 | ATTP_4-40818001 | Neumarkt /Hausruck | 48.2734 | 13.7379 | 10750 | 7957 | NO | 49.7312 | 0 | 0 | 0 | 288.4412 | 1730.6475 | AT31 | A
AT | AT315 | ATAG_4-40704001 | ATTP_4-40704001 | Ebensee | 47.8119 | 13.7817 | 12000 | 8426 | NO | 52.6625 | 0 | 0 | 0 | 305.4425 | 1832.655 | AT31 | A
AT | AT315 | ATAG_4-40719002 | ATTP_4-40719002 | Scharnstein | 47.9157 | 13.9762 | 12500 | 7803 | NO | 48.7688 | 0 | 0 | 0 | 282.8587 | 1697.1525 | AT31 | A
AT | AT313 | ATAG_4-41123001 | ATTP_4-41123001 | Machland Ost Saxen | 48.199 | 14.8006 | 12700 | 6395 | NO | 39.9688 | 0 | 0 | 0 | 231.8187 | 1390.9125 | AT31 | B
AT | AT314 | ATAG_4-40923001 | ATTP_4-40923001 | Windischgarsten | 47.7227 | 14.302 | 16100 | 14227 | YES | 88.9188 | 284.54 | 213.405 | 426.81 | 515.7287 | 3094.3725 | AT31 | B
AT | AT315 | ATAG_4-40720001 | ATTP_4-40720001 | Vorchdorf | 48.0173 | 13.9099 | 17000 | 12942 | NO | 80.8875 | 0 | 0 | 0 | 469.1475 | 2814.885 | AT31 | B
AT | AT311 | ATAG_4-40401001 | ATTP_4-40401001 | Altheim und Umgebung | 48.2603 | 13.2105 | 19000 | 13324 | NO | 83.275 | 0 | 0 | 0 | 482.995 | 2897.97 | AT31 | C
AT | AT313 | ATAG_4-40614001 | ATTP_4-40614001 | Untere Feldaist | 48.3532 | 14.5257 | 21500 | 10056 | YES | 62.85 | 201.12 | 150.84 | 301.68 | 364.53 | 2187.18 | AT31 | A
AT | AT315 | ATAG_4-41710001 | ATTP_4-41710001 | Frankenmarkt | 47.9877 | 13.4485 | 21700 | 11870 | NO | 74.1875 | 0 | 0 | 0 | 430.2875 | 2581.725 | AT31 | A
AT | AT315 | ATAG_4-40702001 | ATTP_4-40702001 | Hallstättersee | 47.6664 | 13.6081 | 22000 | 19765 | YES | 123.5312 | 395.3 | 296.475 | 592.95 | 716.4812 | 4298.8875 | AT31 | A
AT | AT314 | ATAG_4-41503001 | ATTP_4-41503001 | Kurbezirk Bad Hall | 48.049 | 14.2054 | 22000 | 15185 | NO | 94.9062 | 0 | 0 | 0 | 550.4562 | 3302.7375 | AT31 | A
AT | AT312 | ATAG_4-41605001 | ATTP_4-41605001 | Gallneukirchner Becken | 48.3411 | 14.4509 | 22838 | 15199 | YES | 94.9937 | 303.98 | 227.985 | 455.97 | 550.9637 | 3305.7825 | AT31 | A
AT | AT311 | ATAG_4-40831002 | ATTP_4-40831002 | Aschachtal | 48.355 | 13.8706 | 25000 | 18064 | YES | 112.9 | 361.28 | 270.96 | 541.92 | 654.82 | 3928.92 | AT31 | C
AT | AT311 | ATAG_4-41220001 | ATTP_4-41220001 | Mittlere Antiesen | 48.3249 | 13.43 | 25000 | 19244 | NO | 120.275 | 0 | 0 | 0 | 697.595 | 4185.57 | AT31 | B
AT | AT315 | ATAG_4-41715001 | ATTP_4-41715001 | Mondsee-Irrsee | 47.8383 | 13.3547 | 25360 | 19565 | YES | 122.2812 | 391.3 | 293.475 | 586.95 | 709.2313 | 4255.3875 | AT31 | A
AT | AT312 | ATAG_4-41014001 | ATTP_4-41014001 | Unteres Kremstal | 48.1513 | 14.2298 | 26000 | 16705 | YES | 104.4062 | 334.1 | 250.575 | 501.15 | 605.5562 | 3633.3375 | AT31 | B
AT | AT311 | ATAG_4-41422001 | ATTP_4-41422001 | Schärding | 48.4644 | 13.4346 | 27000 | 12088 | YES | 75.55 | 241.76 | 181.32 | 362.64 | 438.19 | 2629.14 | AT31 | A
AT | AT313 | ATAG_4-40601002 | ATTP_4-40601002 | Freistadt | 48.4944 | 14.5065 | 30000 | 27555 | YES | 172.2188 | 551.1 | 413.325 | 826.65 | 998.8687 | 5993.2125 | AT31 | A
AT | AT313 | ATAG_4-41111001 | ATTP_4-41111001 | Mauthausen-Ost | 48.2339 | 14.5571 | 30000 | 32316 | YES | 201.975 | 646.32 | 484.74 | 969.48 | 1171.455 | 7028.73 | AT31 | B
AT | AT313 | ATAG_4-41116001 | ATTP_4-41116001 | Perg | 48.2329 | 14.6453 | 30000 | 22290 | NO | 139.3125 | 0 | 0 | 0 | 808.0125 | 4848.075 | AT31 | B
AT | AT313 | ATAG_4-41307001 | ATTP_4-41307001 | Mühltal | 48.5168 | 14.0329 | 31000 | 23753 | NO | 148.4563 | 0 | 0 | 0 | 861.0462 | 5166.2775 | AT31 | C
AT | AT311 | ATAG_4-40404001 | ATTP_4-40404001 | Braunau | 48.2646 | 13.0596 | 38500 | 38289 | YES | 239.3063 | 765.78 | 574.335 | 1148.67 | 1387.9762 | 8327.8575 | AT31 | A
AT | AT314 | ATAG_4-40922001 | ATTP_4-40922001 | Oberes Kremstal | 48.006 | 14.1181 | 45000 | 26294 | YES | 164.3375 | 525.88 | 394.41 | 788.82 | 953.1575 | 5718.945 | AT31 | C
AT | AT312 | ATAG_4-41811001 | ATTP_4-41811001 | Raum Lambach | 48.0943 | 13.9221 | 47500 | 23748 | YES | 148.425 | 474.96 | 356.22 | 712.44 | 860.865 | 5165.19 | AT31 | A
AT | AT315 | ATAG_4-41738002 | ATTP_4-41738002 | Schwanenstadt | 48.055 | 13.7924 | 50000 | 25682 | NO | 160.5125 | 0 | 0 | 0 | 930.9725 | 5585.835 | AT31 | B
AT | AT311 | ATAG_4-40421001 | ATTP_4-40421001 | Mattig-Hainbach | 48.1248 | 13.1323 | 54000 | 30248 | YES | 189.05 | 604.96 | 453.72 | 907.44 | 1096.49 | 6578.94 | AT31 | C
AT | AT312 | ATAG_4-40509001 | ATTP_4-40509001 | Eferding | 48.323 | 14.0471 | 60000 | 31566 | YES | 197.2875 | 631.32 | 473.49 | 946.98 | 1144.2675 | 6865.605 | AT31 | C
AT | AT315 | ATAG_4-41713002 | ATTP_4-41713002 | Attersee | 47.9682 | 13.6082 | 65000 | 45085 | YES | 281.7812 | 901.7 | 676.275 | 1352.55 | 1634.3312 | 9805.9875 | AT31 | A
AT | AT311 | ATAG_4-40832001 | ATTP_4-40832001 | Trattnachtal | 48.241 | 13.9673 | 65000 | 59299 | YES | 370.6188 | 1185.98 | 889.485 | 1778.97 | 2149.5887 | 12897.5325 | AT31 | C
AT | AT315 | ATAG_4-41711001 | ATTP_4-41711001 | Vöckla - Redl | 48.0211 | 13.5338 | 70000 | 42845 | YES | 267.7812 | 856.9 | 642.675 | 1285.35 | 1553.1312 | 9318.7875 | AT31 | C
AT | AT315 | ATAG_4-41703001 | ATTP_4-41703001 | Ager-West | 48.0154 | 13.7466 | 76000 | 59055 | YES | 369.0938 | 1181.1 | 885.825 | 1771.65 | 2140.7437 | 12844.4625 | AT31 | A
AT | AT311 | ATAG_4-41225001 | ATTP_4-41225001 | Ried und Umgebung | 48.2251 | 13.4791 | 79700 | 40350 | YES | 252.1875 | 807 | 605.25 | 1210.5 | 1462.6875 | 8776.125 | AT31 | A
AT | AT315 | ATAG_4-40703001 | ATTP_4-40703001 | Wolfgangsee-Ischl | 47.7249 | 13.6484 | 100000 | 40144 | YES | 250.9 | 802.88 | 602.16 | 1204.32 | 1455.22 | 8731.32 | AT31 | A
AT | AT315 | ATAG_4-40708001 | ATTP_4-40708001 | Traunsee-Nord | 47.9421 | 13.8032 | 106000 | 81454 | YES | 509.0875 | 1629.08 | 1221.81 | 2443.62 | 2952.7075 | 17716.245 | AT31 | A
AT | AT314 | ATAG_4-40201001 | ATTP_4-40201001 | Steyr und Umgebung | 48.0639 | 14.4328 | 140000 | 101128 | YES | 632.05 | 2022.56 | 1516.92 | 3033.84 | 3665.89 | 21995.34 | AT31 | A
AT | AT312 | ATAG_4-41812001 | ATTP_4-41812001 | Welser Heide | 48.1822 | 14.1375 | 160000 | 167159 | YES | 1044.7438 | 3343.18 | 2507.385 | 5014.77 | 6059.5138 | 36357.0825 | AT31 | B
AT | AT312 | ATAG_4-40502002 | ATTP_4-40502002 | AGRANA | 48.3624 | 14.015 | 205600 | 3080 | NO | 19.25 | 0 | 0 | 0 | 111.65 | 669.9 | AT31 | A
AT | AT312 | ATAG_4-41003001 | ATTP_4-41003001 | Asten - Regionalkläranlage | 48.2366 | 14.4122 | 950000 | 951808 | YES | 5948.8 | 19036.16 | 14277.12 | 28554.24 | 34503.04 | 207018.24 | AT31 | A
AT | AT323 | ATAG_5-A1651372R143 | ATTP_5-A1651372R143 | ARA Annaberg | 47.5371 | 13.4223 | 5700 | 5103 | NO | 31.8938 | 0 | 0 | 0 | 184.9837 | 1109.9025 | AT32 | C
AT | AT323 | ATAG_5-A1705398R154 | ATTP_5-A1705398R154 | ARA Faistenau | 47.7591 | 13.2302 | 6750 | 3500 | NO | 21.875 | 0 | 0 | 0 | 126.875 | 761.25 | AT32 | C
AT | AT322 | ATAG_5-A1780441R157 | ATTP_5-A1780441R157 | ARA Mühlbach | 47.3806 | 13.1497 | 9000 | 4220 | NO | 26.375 | 0 | 0 | 0 | 152.975 | 917.85 | AT32 | C
AT | AT322 | ATAG_5-A1779204R157 | ATTP_5-A1779204R157 | ARA Filzmoos | 47.4294 | 13.5318 | 10000 | 3781 | NO | 23.6312 | 0 | 0 | 0 | 137.0612 | 822.3675 | AT32 | A
AT | AT322 | ATAG_5-A1841691R161 | ATTP_5-A1841691R161 | ARA Rauris | 47.2511 | 12.9863 | 10500 | 7119 | NO | 44.4937 | 0 | 0 | 0 | 258.0637 | 1548.3825 | AT32 | C
AT | AT323 | ATAG_5-A1651838R143 | ATTP_5-A1651838R143 | ARA Abtenau | 47.5921 | 13.3205 | 12088 | 7616 | NO | 47.6 | 0 | 0 | 0 | 276.08 | 1656.48 | AT32 | A
AT | AT322 | ATAG_5-A1781001R157 | ATTP_5-A1781001R157 | ARA Fritztal-Hüttau | 47.4219 | 13.2967 | 14000 | 9829 | NO | 61.4313 | 0 | 0 | 0 | 356.3012 | 2137.8075 | AT32 | C
AT | AT323 | ATAG_5-A1698988R154 | ATTP_5-A1698988R154 | ARA Wallersee-Nord-Neumarkt | 47.9437 | 13.2079 | 15000 | 12511 | NO | 78.1938 | 0 | 0 | 0 | 453.5238 | 2721.1425 | AT32 | B
AT | AT322 | ATAG_5-A1779078R157 | ATTP_5-A1779078R157 | ARA Großarlertal | 47.2799 | 13.2171 | 18000 | 11144 | NO | 69.65 | 0 | 0 | 0 | 403.97 | 2423.82 | AT32 | A
AT | AT323 | ATAG_5-A1703863R154 | ATTP_5-A1703863R154 | ARA Fuschlsee-Thalgau | 47.8378 | 13.2743 | 23500 | 20592 | NO | 128.7 | 0 | 0 | 0 | 746.46 | 4478.76 | AT32 | A
AT | AT323 | ATAG_5-A1700495R154 | ATTP_5-A1700495R154 | ARA Pladenbach | 47.9929 | 12.8701 | 24000 | 22497 | NO | 140.6063 | 0 | 0 | 0 | 815.5163 | 4893.0975 | AT32 | B
AT | AT322 | ATAG_5-A1843680R161 | ATTP_5-A1843680R161 | ARA Saalachtal-Unken | 47.6635 | 12.7538 | 24500 | 9970 | YES | 62.3125 | 199.4 | 149.55 | 299.1 | 361.4125 | 2168.475 | AT32 | C
AT | AT321 | ATAG_5-A1805835R161 | ATTP_5-A1805835R161 | ARA St.Michael i.Lg. | 47.0929 | 13.6468 | 25000 | 12486 | NO | 78.0375 | 0 | 0 | 0 | 452.6175 | 2715.705 | AT32 | A
AT | AT322 | ATAG_5-A1848116R161 | ATTP_5-A1848116R161 | ARA Unterpinzgau-Bruck | 47.2828 | 12.8672 | 25000 | 9370 | NO | 58.5625 | 0 | 0 | 0 | 339.6625 | 2037.975 | AT32 | A
AT | AT322 | ATAG_5-A1844700R161 | ATTP_5-A1844700R161 | ARA Oberpinzgau Mitte-Niedernsill | 47.2815 | 12.6677 | 27000 | 24214 | YES | 151.3375 | 484.28 | 363.21 | 726.42 | 877.7575 | 5266.545 | AT32 | C
AT | AT323 | ATAG_5-A1651310R143 | ATTP_5-A1651310R143 | ARA Tennengau-Süd-Kuchl | 47.6542 | 13.1222 | 32000 | 18648 | YES | 116.55 | 372.96 | 279.72 | 559.44 | 675.99 | 4055.94 | AT32 | A
AT | AT321 | ATAG_5-A2444685 | ATTP_5-A2444685 | ARA Zentralraum Lungau | 47.1179 | 13.8143 | 32000 | 22707 | YES | 141.9188 | 454.14 | 340.605 | 681.21 | 823.1288 | 4938.7725 | AT32 | B
AT | AT323 | ATAG_5-A1700419R154 | ATTP_5-A1700419R154 | ARA Wallersee-Süd-Seekirchen | 47.8851 | 13.1206 | 35000 | 29777 | YES | 186.1063 | 595.54 | 446.655 | 893.31 | 1079.4162 | 6476.4975 | AT32 | A
AT | AT322 | ATAG_5-A1842420R161 | ATTP_5-A1842420R161 | ARA Bramberg, Oberpinzgau West | 47.2794 | 12.3967 | 40000 | 20972 | YES | 131.075 | 419.44 | 314.58 | 629.16 | 760.235 | 4561.41 | AT32 | B
AT | AT323 | ATAG_5-A1700239R154 | ATTP_5-A1700239R154 | ARA Trumerseen | 47.9812 | 13.0865 | 40000 | 20156 | YES | 125.975 | 403.12 | 302.34 | 604.68 | 730.655 | 4383.93 | AT32 | C
AT | AT322 | ATAG_5-A1780627R157 | ATTP_5-A1780627R157 | ARA Gasteinertal | 47.2648 | 13.0804 | 45000 | 32367 | YES | 202.2938 | 647.34 | 485.505 | 971.01 | 1173.3038 | 7039.8225 | AT32 | C
AT | AT322 | ATAG_5-A1824831R161 | ATTP_5-A1824831R161 | ARA Saalbach | 47.3718 | 12.6924 | 49000 | 25885 | YES | 161.7812 | 517.7 | 388.275 | 776.55 | 938.3312 | 5629.9875 | AT32 | C
AT | AT322 | ATAG_5-A1844668R161 | ATTP_5-A1844668R161 | ARA Zeller Becken | 47.2831 | 12.7913 | 70000 | 44606 | NO | 278.7875 | 0 | 0 | 0 | 1616.9675 | 9701.805 | AT32 | C
AT | AT322 | ATAG_5-A1836862R161 | ATTP_5-A1836862R161 | ARA Saalachtal-Saalfelden | 47.4632 | 12.8266 | 80000 | 77154 | YES | 482.2125 | 1543.08 | 1157.31 | 2314.62 | 2796.8325 | 16780.995 | AT32 | C
AT | AT322 | ATAG_5-A1779244R157 | ATTP_5-A1779244R157 | ARA Salzach-Pongau | 47.4386 | 13.2109 | 125000 | 87380 | NO | 546.125 | 0 | 0 | 0 | 3167.525 | 19005.15 | AT32 | A
AT | AT322 | ATAG_5-A1777733R157 | ATTP_5-A1777733R157 | ARA Salzburger Ennstal | 47.387 | 13.4954 | 125000 | 49826 | YES | 311.4125 | 996.52 | 747.39 | 1494.78 | 1806.1925 | 10837.155 | AT32 | C
AT | AT323 | ATAG_5-A1699622R154 | ATTP_5-A1699622R154 | ARA Siggerwiesen | 47.8597 | 13.0025 | 680000 | 509019 | YES | 3181.3688 | 10180.38 | 7635.285 | 15270.57 | 18451.9388 | 110711.6325 | AT32 | A
AT | AT225 | ATAG_6-M3306173R0 | ATTP_6-M3306173R0 | Wies | 46.721 | 15.2801 | 5000 | 3395 | NO | 21.2188 | 0 | 0 | 0 | 123.0687 | 738.4125 | AT22 | B
AT | AT224 | ATAG_6-M3192786R0 | ATTP_6-M3192786R0 | Ilztal | 47.1384 | 15.7908 | 5000 | 3980 | NO | 24.875 | 0 | 0 | 0 | 144.275 | 865.65 | AT22 | B
AT | AT224 | ATAG_6-M3411539R0 | ATTP_6-M3411539R0 | Kaindorf-RHV | 47.2149 | 15.9104 | 5000 | 7164 | NO | 44.775 | 0 | 0 | 0 | 259.695 | 1558.17 | AT22 | B
AT | AT223 | ATAG_6-M3426844R0 | ATTP_6-M3426844R0 | Kalwang | 47.418 | 14.7645 | 5000 | 1930 | NO | 12.0625 | 0 | 0 | 0 | 69.9625 | 419.775 | AT22 | B
AT | AT222 | ATAG_6-M3464616R0 | ATTP_6-M3464616R0 | Haus | 47.4143 | 13.7726 | 5400 | 4287 | NO | 26.7938 | 0 | 0 | 0 | 155.4038 | 932.4225 | AT22 | B
AT | AT224 | ATAG_6-M3326085R0 | ATTP_6-M3326085R0 | Stubenberg | 47.2368 | 15.7967 | 5500 | 2514 | NO | 15.7125 | 0 | 0 | 0 | 91.1325 | 546.795 | AT22 | A
AT | AT222 | ATAG_6-M3222800R0 | ATTP_6-M3222800R0 | Aigen im Ennstal | 47.5443 | 14.146 | 6000 | 4866 | NO | 30.4125 | 0 | 0 | 0 | 176.3925 | 1058.355 | AT22 | B
AT | AT224 | ATAG_6-M3719878R0 | ATTP_6-M3719878R0 | Sinabelkirchen | 47.0975 | 15.8322 | 6250 | 5023 | NO | 31.3938 | 0 | 0 | 0 | 182.0838 | 1092.5025 | AT22 | B
AT | AT224 | ATAG_6-M3532431R0 | ATTP_6-M3532431R0 | St.Stefan im Rosental | 46.8961 | 15.7197 | 6300 | 6884 | NO | 43.025 | 0 | 0 | 0 | 249.545 | 1497.27 | AT22 | B
AT | AT225 | ATAG_6-M3456540R0 | ATTP_6-M3456540R0 | Sulmeck-Greith-Gasselsdorf | 46.7347 | 15.3364 | 6500 | 9543 | NO | 59.6438 | 0 | 0 | 0 | 345.9338 | 2075.6025 | AT22 | C
AT | AT224 | ATAG_6-M3756860R0 | ATTP_6-M3756860R0 | Grosssteinbach | 47.1427 | 15.8885 | 6800 | 5058 | NO | 31.6125 | 0 | 0 | 0 | 183.3525 | 1100.115 | AT22 | B
AT | AT225 | ATAG_6-M3280413R0 | ATTP_6-M3280413R0 | Heiligenkreuz am Waasen | 46.9525 | 15.5908 | 7000 | 7503 | NO | 46.8938 | 0 | 0 | 0 | 271.9838 | 1631.9025 | AT22 | B
AT | AT341 | ATAG_8-Bezau | ATTP_8-Bezau | Bezau | 47.3864 | 9.8838 | 37750 | 16051 | YES | 100.3188 | 321.02 | 240.765 | 481.53 | 581.8487 | 3491.0925 | AT34 | A
AT | AT342 | ATAG_8-Leiblachtal | ATTP_8-Leiblachtal | Leiblachtal | 47.5332 | 9.7366 | 41500 | 33402 | YES | 208.7625 | 668.04 | 501.03 | 1002.06 | 1210.8225 | 7264.935 | AT34 | A
AT | AT341 | ATAG_8-Egg | ATTP_8-Egg | Egg | 47.4339 | 9.8936 | 42300 | 9740 | NO | 60.875 | 0 | 0 | 0 | 353.075 | 2118.45 | AT34 | A
AT | AT341 | ATAG_8-Lech | ATTP_8-Lech | Lech | 47.2194 | 10.153 | 50000 | 27810 | YES | 173.8125 | 556.2 | 417.15 | 834.3 | 1008.1125 | 6048.675 | AT34 | A
AT | AT342 | ATAG_8-Walgau | ATTP_8-Walgau | Walgau | 47.223 | 9.6558 | 56250 | 24652 | YES | 154.075 | 493.04 | 369.78 | 739.56 | 893.635 | 5361.81 | AT34 | A
AT | AT341 | ATAG_8-Montafon | ATTP_8-Montafon | Montafon | 47.1169 | 9.8561 | 62500 | 35427 | YES | 221.4188 | 708.54 | 531.405 | 1062.81 | 1284.2287 | 7705.3725 | AT34 | B
AT | AT342 | ATAG_8-Bregenz | ATTP_8-Bregenz | Bregenz | 47.5045 | 9.7067 | 75000 | 38372 | YES | 239.825 | 767.44 | 575.58 | 1151.16 | 1390.985 | 8345.91 | AT34 | B
AT | AT341 | ATAG_8-Ludesch | ATTP_8-Ludesch | Ludesch | 47.1746 | 9.7701 | 108000 | 69454 | YES | 434.0875 | 1389.08 | 1041.81 | 2083.62 | 2517.7075 | 15106.245 | AT34 | A
AT | AT342 | ATAG_8-Dornbirn | ATTP_8-Dornbirn | Dornbirn | 47.4317 | 9.7259 | 150000 | 86246 | YES | 539.0375 | 1724.92 | 1293.69 | 2587.38 | 3126.4175 | 18758.505 | AT34 | A
AT | AT342 | ATAG_8-Hohenems | ATTP_8-Hohenems | Hohenems | 47.3656 | 9.6631 | 170000 | 74655 | YES | 466.5938 | 1493.1 | 1119.825 | 2239.65 | 2706.2437 | 16237.4625 | AT34 | A
AT | AT342 | ATAG_8-Hofsteig | ATTP_8-Hofsteig | Hofsteig | 47.4859 | 9.6765 | 271600 | 149292 | YES | 933.075 | 2985.84 | 2239.38 | 4478.76 | 5411.835 | 32471.01 | AT34 | A
AT | AT342 | ATAG_8-Meiningen | ATTP_8-Meiningen | Meiningen | 47.3085 | 9.5897 | 380000 | 267697 | YES | 1673.1063 | 5353.94 | 4015.455 | 8030.91 | 9704.0163 | 58224.0975 | AT34 | B
AT | AT130 | ATAG_9-HKA-Simmering | ATTP_9-HKA-Simmering | Hauptkläranlage Wien | 48.1723 | 16.4653 | 4000000 | 3118566 | YES | 19491.0375 | 62371.32 | 46778.49 | 93556.98 | 113048.0175 | 678288.105 | AT13 | A
AT | AT224 | ATAG_6-M3231297R0 | ATTP_6-M3231297R0 | Gnas | 46.8549 | 15.8255 | 7000 | 5045 | NO | 31.5312 | 0 | 0 | 0 | 182.8812 | 1097.2875 | AT22 | C
AT | AT223 | ATAG_6-M3449658R0 | ATTP_6-M3449658R0 | Wartberg/Mürz-II | 47.5241 | 15.4656 | 17000 | 25730 | YES | 160.8125 | 514.6 | 385.95 | 771.9 | 932.7125 | 5596.275 | AT22 | C
AT | AT224 | ATAG_6-M3756265R0 | ATTP_6-M3756265R0 | Bad Gleichenberg-Neu | 46.8453 | 15.8956 | 17500 | 7479 | NO | 46.7438 | 0 | 0 | 0 | 271.1138 | 1626.6825 | AT22 | B
AT | AT225 | ATAG_6-M3384279R0 | ATTP_6-M3384279R0 | Stainz | 46.8857 | 15.2881 | 20500 | 16135 | YES | 100.8438 | 322.7 | 242.025 | 484.05 | 584.8937 | 3509.3625 | AT22 | B
AT | AT223 | ATAG_6-M3290534R0 | ATTP_6-M3290534R0 | Trofaiach | 47.414 | 15.02 | 21000 | 16134 | YES | 100.8375 | 322.68 | 242.01 | 484.02 | 584.8575 | 3509.145 | AT22 | A
AT | AT226 | ATAG_6-M3699458R0 | ATTP_6-M3699458R0 | Murau | 47.1083 | 14.1904 | 22000 | 9290 | NO | 58.0625 | 0 | 0 | 0 | 336.7625 | 2020.575 | AT22 | A
AT | AT225 | ATAG_6-M3444791R0 | ATTP_6-M3444791R0 | Frauental | 46.8286 | 15.2715 | 22000 | 18256 | NO | 114.1 | 0 | 0 | 0 | 661.78 | 3970.68 | AT22 | B
AT | AT223 | ATAG_6-M3406862R0 | ATTP_6-M3406862R0 | St.Michael | 47.3373 | 15.0321 | 23000 | 12973 | YES | 81.0812 | 259.46 | 194.595 | 389.19 | 470.2713 | 2821.6275 | AT22 | A
AT | AT223 | ATAG_6-M3450226R0 | ATTP_6-M3450226R0 | Langenwang/Mürz-I | 47.5604 | 15.6083 | 24000 | 29678 | YES | 185.4875 | 593.56 | 445.17 | 890.34 | 1075.8275 | 6454.965 | AT22 | A
AT | AT225 | ATAG_6-M4343579 | ATTP_6-M4343579 | Köflach-Gradnerbachtal | 47.0625 | 15.0972 | 25000 | 21927 | YES | 137.0438 | 438.54 | 328.905 | 657.81 | 794.8537 | 4769.1225 | AT22 | A
AT | AT226 | ATAG_6-M3751070R0 | ATTP_6-M3751070R0 | Judenburg | 47.1703 | 14.6738 | 25000 | 18149 | YES | 113.4312 | 362.98 | 272.235 | 544.47 | 657.9012 | 3947.4075 | AT22 | A
AT | AT222 | ATAG_6-M3691867R0 | ATTP_6-M3691867R0 | Bad Aussee | 47.6017 | 13.7587 | 25000 | 17613 | NO | 110.0813 | 0 | 0 | 0 | 638.4713 | 3830.8275 | AT22 | B
AT | AT223 | ATAG_6-M3646738R0 | ATTP_6-M3646738R0 | St.Marein/Mürz-III | 47.4696 | 15.3605 | 26000 | 18784 | YES | 117.4 | 375.68 | 281.76 | 563.52 | 680.92 | 4085.52 | AT22 | A
AT | AT221 | ATAG_6-M3263261R0 | ATTP_6-M3263261R0 | Frohnleiten | 47.2559 | 15.3153 | 28000 | 7709 | NO | 48.1813 | 0 | 0 | 0 | 279.4513 | 1676.7075 | AT22 | C
AT | AT226 | ATAG_6-M3685913R0 | ATTP_6-M3685913R0 | Zeltweg | 47.1877 | 14.7594 | 30000 | 21157 | YES | 132.2313 | 423.14 | 317.355 | 634.71 | 766.9412 | 4601.6475 | AT22 | A
AT | AT224 | ATAG_6-M3255142R0 | ATTP_6-M3255142R0 | Weiz | 47.2064 | 15.6342 | 30000 | 20574 | YES | 128.5875 | 411.48 | 308.61 | 617.22 | 745.8075 | 4474.845 | AT22 | A
AT | AT222 | ATAG_6-M3517936R0 | ATTP_6-M3517936R0 | Schladming | 47.3979 | 13.7039 | 31000 | 19040 | NO | 119 | 0 | 0 | 0 | 690.2 | 4141.2 | AT22 | A
AT | AT224 | ATAG_6-M3407477R0 | ATTP_6-M3407477R0 | Gleisdorf | 47.0931 | 15.7132 | 32000 | 39806 | YES | 248.7875 | 796.12 | 597.09 | 1194.18 | 1442.9675 | 8657.805 | AT22 | A
AT | AT225 | ATAG_6-M3690570R0 | ATTP_6-M3690570R0 | Voitsberg | 47.0305 | 15.1853 | 32000 | 19723 | YES | 123.2688 | 394.46 | 295.845 | 591.69 | 714.9588 | 4289.7525 | AT22 | A
AT | AT224 | ATAG_6-M3710856R0 | ATTP_6-M3710856R0 | Feldbach-Raabau | 46.953 | 15.9261 | 35000 | 29543 | YES | 184.6437 | 590.86 | 443.145 | 886.29 | 1070.9337 | 6425.6025 | AT22 | B
AT | AT223 | ATAG_6-M3586337R0 | ATTP_6-M3586337R0 | Bruck | 47.394 | 15.2861 | 36000 | 28458 | YES | 177.8625 | 569.16 | 426.87 | 853.74 | 1031.6025 | 6189.615 | AT22 | A
AT | AT224 | ATAG_6-M3474844R0 | ATTP_6-M3474844R0 | Fürstenfeld | 47.0445 | 16.0995 | 38000 | 31512 | NO | 196.95 | 0 | 0 | 0 | 1142.31 | 6853.86 | AT22 | B
AT | AT225 | ATAG_6-M3679960R0 | ATTP_6-M3679960R0 | Söding | 46.9904 | 15.2909 | 38000 | 22194 | YES | 138.7125 | 443.88 | 332.91 | 665.82 | 804.5325 | 4827.195 | AT22 | B
AT | AT225 | ATAG_6-M3358117R0 | ATTP_6-M3358117R0 | Strass | 46.7174 | 15.6245 | 39000 | 36021 | YES | 225.1313 | 720.42 | 540.315 | 1080.63 | 1305.7613 | 7834.5675 | AT22 | B
AT | AT223 | ATAG_6-M3647058R0 | ATTP_6-M3647058R0 | Kapfenberg/Mürz-IV | 47.4297 | 15.2713 | 49000 | 42850 | NO | 267.8125 | 0 | 0 | 0 | 1553.3125 | 9319.875 | AT22 | A
AT | AT225 | ATAG_6-M3453257R0 | ATTP_6-M3453257R0 | Wagna-Leibnitz | 46.7646 | 15.5688 | 50000 | 38125 | YES | 238.2812 | 762.5 | 571.875 | 1143.75 | 1382.0312 | 8292.1875 | AT22 | A
AT | AT224 | ATAG_6-M3400230R0 | ATTP_6-M3400230R0 | Hartberg | 47.271 | 15.9797 | 69000 | 62477 | YES | 390.4813 | 1249.54 | 937.155 | 1874.31 | 2264.7913 | 13588.7475 | AT22 | B
AT | AT226 | ATAG_6-M4274145 | ATTP_6-M4274145 | Knittelfeld | 47.2211 | 14.8436 | 70000 | 90944 | NO | 568.4 | 0 | 0 | 0 | 3296.72 | 19780.32 | AT22 | A
AT | AT223 | ATAG_6-M3409760R0 | ATTP_6-M3409760R0 | Leoben | 47.3873 | 15.1065 | 90000 | 44165 | YES | 276.0312 | 883.3 | 662.475 | 1324.95 | 1600.9812 | 9605.8875 | AT22 | A
AT | AT225 | ATAG_6-M3223510R0 | ATTP_6-M3223510R0 | Wildon | 46.879 | 15.5305 | 120000 | 83033 | YES | 518.9563 | 1660.66 | 1245.495 | 2490.99 | 3009.9463 | 18059.6775 | AT22 | B
AT | AT226 | ATAG_6-M3641482R0 | ATTP_6-M3641482R0 | Pöls-VKA | 47.2178 | 14.5966 | 198667 | 9000 | NO | 56.25 | 0 | 0 | 0 | 326.25 | 1957.5 | AT22 | A
AT | AT221 | ATAG_6-M3489301R0 | ATTP_6-M3489301R0 | Graz-Gössendorf | 46.9964 | 15.472 | 500000 | 492391 | YES | 3077.4438 | 9847.82 | 7385.865 | 14771.73 | 17849.1738 | 107095.0425 | AT22 | A
AT | AT221 | ATAG_6-M3631054R0 | ATTP_6-M3631054R0 | Gratkorn | 47.1341 | 15.3341 | 533000 | 25000 | NO | 156.25 | 0 | 0 | 0 | 906.25 | 5437.5 | AT22 | A
AT | AT334 | ATAG_7-7604508 | ATTP_7-7604508 | Fließ | 47.1251 | 10.5819 | 5000 | 3665 | NO | 22.9062 | 0 | 0 | 0 | 132.8562 | 797.1375 | AT33 | C
AT | AT333 | ATAG_7-7724703 | ATTP_7-7724703 | St. Jakob i.D. | 46.9153 | 12.3694 | 5000 | 1608 | YES | 10.05 | 32.16 | 24.12 | 48.24 | 58.29 | 349.74 | AT33 | C
AT | AT332 | ATAG_7-7330305 | ATTP_7-7330305 | Mühlbachl | 47.1399 | 11.4527 | 10000 | 8371 | YES | 52.3188 | 167.42 | 125.565 | 251.13 | 303.4487 | 1820.6925 | AT33 | A
AT | AT334 | ATAG_7-7615507 | ATTP_7-7615507 | Nauders | 46.9073 | 10.4961 | 10000 | 4665 | YES | 29.1562 | 93.3 | 69.975 | 139.95 | 169.1062 | 1014.6375 | AT33 | C
AT | AT333 | ATAG_7-7704702 | ATTP_7-7704702 | Anras | 46.7626 | 12.5666 | 14000 | 14228 | NO | 88.925 | 0 | 0 | 0 | 515.765 | 3094.59 | AT33 | C
AT | AT335 | ATAG_7-7529109 | ATTP_7-7529109 | Walchsee | 47.6497 | 12.3469 | 14850 | 9373 | NO | 58.5813 | 0 | 0 | 0 | 339.7713 | 2038.6275 | AT33 | A
AT | AT335 | ATAG_7-7419207 | ATTP_7-7419207 | Waidring | 47.5857 | 12.6006 | 15100 | 6747 | YES | 42.1688 | 134.94 | 101.205 | 202.41 | 244.5788 | 1467.4725 | AT33 | C
AT | AT334 | ATAG_7-7623505 | ATTP_7-7623505 | See | 47.0919 | 10.4784 | 16137 | 5041 | NO | 31.5062 | 0 | 0 | 0 | 182.7362 | 1096.4175 | AT33 | B
AT | AT335 | ATAG_7-7518105 | ATTP_7-7518105 | Niederndorf | 47.644 | 12.1988 | 18000 | 10312 | YES | 64.45 | 206.24 | 154.68 | 309.36 | 373.81 | 2242.86 | AT33 | B
AT | AT331 | ATAG_7-7830402 | ATTP_7-7830402 | Stanzach | 47.3971 | 10.5754 | 19000 | 12172 | YES | 76.075 | 243.44 | 182.58 | 365.16 | 441.235 | 2647.41 | AT33 | C
AT | AT335 | ATAG_7-7403201 | ATTP_7-7403201 | Fieberbrunn | 47.4963 | 12.4919 | 19000 | 12650 | YES | 79.0625 | 253 | 189.75 | 379.5 | 458.5625 | 2751.375 | AT33 | C
AT | AT332 | ATAG_7-7355306 | ATTP_7-7355306 | Steinach | 47.0982 | 11.466 | 20000 | 8002 | YES | 50.0125 | 160.04 | 120.03 | 240.06 | 290.0725 | 1740.435 | AT33 | A
AT | AT334 | ATAG_7-7208605 | ATTP_7-7208605 | Längenfeld | 47.1055 | 10.9542 | 20000 | 9570 | YES | 59.8125 | 191.4 | 143.55 | 287.1 | 346.9125 | 2081.475 | AT33 | B
AT | AT331 | ATAG_7-7829403 | ATTP_7-7829403 | Schattwald | 47.5243 | 10.4528 | 20100 | 16553 | YES | 103.4563 | 331.06 | 248.295 | 496.59 | 600.0463 | 3600.2775 | AT33 | B
AT | AT334 | ATAG_7-7218603 | ATTP_7-7218603 | Sautens | 47.2151 | 10.8623 | 20200 | 19256 | YES | 120.35 | 385.12 | 288.84 | 577.68 | 698.03 | 4188.18 | AT33 | A
AT | AT334 | ATAG_7-7629506 | ATTP_7-7629506 | Tösens | 47.0359 | 10.6293 | 20500 | 13416 | YES | 83.85 | 268.32 | 201.24 | 402.48 | 486.33 | 2917.98 | AT33 | C
AT | AT335 | ATAG_7-7412203 | ATTP_7-7412203 | Kössen | 47.675 | 12.3967 | 21000 | 11286 | YES | 70.5375 | 225.72 | 169.29 | 338.58 | 409.1175 | 2454.705 | AT33 | B
AT | AT331 | ATAG_7-7807404 | ATTP_7-7807404 | Ehrwald | 47.4222 | 10.9184 | 24500 | 13793 | YES | 86.2062 | 275.86 | 206.895 | 413.79 | 499.9962 | 2999.9775 | AT33 | C
AT | AT332 | ATAG_7-7351308 | ATTP_7-7351308 | Seefeld | 47.3414 | 11.1972 | 26000 | 13036 | NO | 81.475 | 0 | 0 | 0 | 472.555 | 2835.33 | AT33 | A
AT | AT334 | ATAG_7-7224609 | ATTP_7-7224609 | Wenns | 47.1735 | 10.7401 | 27500 | 8989 | YES | 56.1813 | 179.78 | 134.835 | 269.67 | 325.8512 | 1955.1075 | AT33 | B
AT | AT335 | ATAG_7-7420206 | ATTP_7-7420206 | Westendorf | 47.4352 | 12.1927 | 28000 | 12325 | YES | 77.0312 | 246.5 | 184.875 | 369.75 | 446.7812 | 2680.6875 | AT33 | C
AT | AT334 | ATAG_7-7619503 | ATTP_7-7619503 | Prutz | 47.092 | 10.668 | 28000 | 16526 | YES | 103.2875 | 330.52 | 247.89 | 495.78 | 599.0675 | 3594.405 | AT33 | C
AT | AT334 | ATAG_7-7630501 | ATTP_7-7630501 | Zams | 47.1685 | 10.5958 | 33000 | 30843 | YES | 192.7687 | 616.86 | 462.645 | 925.29 | 1118.0587 | 6708.3525 | AT33 | A
AT | AT335 | ATAG_7-7526104 | ATTP_7-7526104 | Söll | 47.5198 | 12.1972 | 35000 | 17400 | YES | 108.75 | 348 | 261 | 522 | 630.75 | 3784.5 | AT33 | C
AT | AT333 | ATAG_7-7717704 | ATTP_7-7717704 | Huben | 46.9232 | 12.5925 | 37000 | 17203 | YES | 107.5188 | 344.06 | 258.045 | 516.09 | 623.6087 | 3741.6525 | AT33 | C
AT | AT334 | ATAG_7-7605502 | ATTP_7-7605502 | Flirsch | 47.1344 | 10.4218 | 38000 | 16665 | YES | 104.1562 | 333.3 | 249.975 | 499.95 | 604.1062 | 3624.6375 | AT33 | B
AT | AT335 | ATAG_7-7404205 | ATTP_7-7404205 | Going | 47.5189 | 12.3676 | 39470 | 24286 | YES | 151.7875 | 485.72 | 364.29 | 728.58 | 880.3675 | 5282.205 | AT33 | A
AT | AT335 | ATAG_7-7520101 | ATTP_7-7520101 | Radfeld | 47.4587 | 11.9318 | 40000 | 36826 | YES | 230.1625 | 736.52 | 552.39 | 1104.78 | 1334.9425 | 8009.655 | AT33 | C
AT | AT332 | ATAG_7-7356304 | ATTP_7-7356304 | Stubaital | 47.1592 | 11.3613 | 40000 | 33911 | NO | 211.9438 | 0 | 0 | 0 | 1229.2738 | 7375.6425 | AT33 | B
AT | AT332 | ATAG_7-7357321 | ATTP_7-7357321 | Telfs | 47.3123 | 11.1113 | 40000 | 36084 | YES | 225.525 | 721.68 | 541.26 | 1082.52 | 1308.045 | 7848.27 | AT33 | A
AT | AT334 | ATAG_7-7221602 | ATTP_7-7221602 | Stams | 47.2849 | 10.9882 | 41000 | 27376 | YES | 171.1 | 547.52 | 410.64 | 821.28 | 992.38 | 5954.28 | AT33 | A
AT | AT334 | ATAG_7-7203601 | ATTP_7-7203601 | Imst | 47.2192 | 10.751 | 46000 | 40107 | YES | 250.6688 | 802.14 | 601.605 | 1203.21 | 1453.8788 | 8723.2725 | AT33 | A
AT | AT335 | ATAG_7-7411204 | ATTP_7-7411204 | Kitzbühel | 47.4647 | 12.3841 | 46550 | 20511 | YES | 128.1937 | 410.22 | 307.665 | 615.33 | 743.5237 | 4461.1425 | AT33 | A
AT | AT335 | ATAG_7-7513103 | ATTP_7-7513103 | Kufstein | 47.604 | 12.188 | 49700 | 42509 | YES | 265.6813 | 850.18 | 637.635 | 1275.27 | 1540.9513 | 9245.7075 | AT33 | A
AT | AT334 | ATAG_7-7608504 | ATTP_7-7608504 | Ischgl | 47.0248 | 10.3078 | 50000 | 24732 | YES | 154.575 | 494.64 | 370.98 | 741.96 | 896.535 | 5379.21 | AT33 | C
AT | AT313 | ATAG_4-40608002 | ATTP_4-40608002 | Königswiesen | 48.395 | 14.8282 | 5000 | 2915 | NO | 18.2188 | 0 | 0 | 0 | 105.6687 | 634.0125 | AT31 | C
AT | AT311 | ATAG_4-41425002 | ATTP_4-41425002 | Suben-St.Marienkirchen | 48.4073 | 13.4353 | 5500 | 4877 | NO | 30.4813 | 0 | 0 | 0 | 176.7912 | 1060.7475 | AT31 | A
AT | AT313 | ATAG_4-41627001 | ATTP_4-41627001 | Mittleres Rodltal | 48.4591 | 14.2671 | 5500 | 5658 | NO | 35.3625 | 0 | 0 | 0 | 205.1025 | 1230.615 | AT31 | A
AT | AT311 | ATAG_4-40811002 | ATTP_4-40811002 | Mittleres Trattnachtal | 48.2241 | 13.7346 | 5625 | 3941 | NO | 24.6312 | 0 | 0 | 0 | 142.8612 | 857.1675 | AT31 | A
AT | AT311 | ATAG_4-40816001 | ATTP_4-40816001 | Natternbach-Neukirchen-Eschenau | 48.3846 | 13.754 | 6000 | 4199 | NO | 26.2438 | 0 | 0 | 0 | 152.2138 | 913.2825 | AT31 | C
AT | AT311 | ATAG_4-40433001 | ATTP_4-40433001 | Polling und Umgebung | 48.2319 | 13.2722 | 6300 | 3973 | NO | 24.8313 | 0 | 0 | 0 | 144.0213 | 864.1275 | AT31 | B
AT | AT315 | ATAG_4-41701001 | ATTP_4-41701001 | Ampflwang | 48.0693 | 13.5699 | 6600 | 4427 | NO | 27.6688 | 0 | 0 | 0 | 160.4788 | 962.8725 | AT31 | C
AT | AT311 | ATAG_4-40806002 | ATTP_4-40806002 | Gaspoltshofen | 48.1559 | 13.765 | 6700 | 3366 | NO | 21.0375 | 0 | 0 | 0 | 122.0175 | 732.105 | AT31 | C
AT | AT313 | ATAG_4-41342001 | ATTP_4-41342001 | Ulrichsberg | 48.6645 | 13.9296 | 6700 | 7686 | NO | 48.0375 | 0 | 0 | 0 | 278.6175 | 1671.705 | AT31 | C
AT | AT333 | ATAG_7-7707701 | ATTP_7-7707701 | Dölsach | 46.8133 | 12.8362 | 56800 | 45621 | YES | 285.1313 | 912.42 | 684.315 | 1368.63 | 1653.7613 | 9922.5675 | AT33 | A
AT | AT332 | ATAG_7-7369303 | ATTP_7-7369303 | Zirl | 47.2649 | 11.2889 | 61500 | 51449 | YES | 321.5563 | 1028.98 | 771.735 | 1543.47 | 1865.0262 | 11190.1575 | AT33 | C
AT | AT335 | ATAG_7-7410202 | ATTP_7-7410202 | Kirchdorf | 47.5957 | 12.4737 | 70000 | 29051 | YES | 181.5687 | 581.02 | 435.765 | 871.53 | 1053.0987 | 6318.5925 | AT33 | C
AT | AT331 | ATAG_7-7833401 | ATTP_7-7833401 | Vils | 47.554 | 10.6583 | 71670 | 65476 | YES | 409.225 | 1309.52 | 982.14 | 1964.28 | 2373.505 | 14241.03 | AT33 | C
AT | AT334 | ATAG_7-7220607 | ATTP_7-7220607 | Sölden | 46.9917 | 11.0125 | 75000 | 22056 | YES | 137.85 | 441.12 | 330.84 | 661.68 | 799.53 | 4797.18 | AT33 | C
AT | AT335 | ATAG_7-7926110 | ATTP_7-7926110 | Schwaz | 47.3626 | 11.7256 | 85000 | 65631 | YES | 410.1937 | 1312.62 | 984.465 | 1968.93 | 2379.1237 | 14274.7425 | AT33 | A
AT | AT335 | ATAG_7-7511102 | ATTP_7-7511102 | Kirchbichl | 47.5349 | 12.1086 | 100000 | 70681 | YES | 441.7562 | 1413.62 | 1060.215 | 2120.43 | 2562.1862 | 15373.1175 | AT33 | C
AT | AT332 | ATAG_7-7309302 | ATTP_7-7309302 | Fritzens | 47.3051 | 11.6085 | 120000 | 73092 | YES | 456.825 | 1461.84 | 1096.38 | 2192.76 | 2649.585 | 15897.51 | AT33 | C
AT | AT335 | ATAG_7-7930111 | ATTP_7-7930111 | Strass | 47.4026 | 11.8354 | 167000 | 151735 | YES | 948.3438 | 3034.7 | 2276.025 | 4552.05 | 5500.3937 | 33002.3625 | AT33 | A
AT | AT332 | ATAG_7-7101301 | ATTP_7-7101301 | Innsbruck | 47.2637 | 11.4466 | 400000 | 281657 | YES | 1760.3563 | 5633.14 | 4224.855 | 8449.71 | 10210.0662 | 61260.3975 | AT33 | A
AT | AT311 | ATAG_4-41402001 | ATTP_4-41402001 | Andorf | 48.3816 | 13.5701 | 6850 | 5153 | NO | 32.2063 | 0 | 0 | 0 | 186.7963 | 1120.7775 | AT31 | B
AT | AT313 | ATAG_4-40620001 | ATTP_4-40620001 | Kettenbach I | 48.3222 | 14.6301 | 7000 | 3749 | NO | 23.4313 | 0 | 0 | 0 | 135.9013 | 815.4075 | AT31 | A
AT | AT313 | ATAG_4-41105004 | ATTP_4-41105004 | Grein | 48.2318 | 14.8752 | 7500 | 3587 | NO | 22.4187 | 0 | 0 | 0 | 130.0288 | 780.1725 | AT31 | B
AT | AT313 | ATAG_4-41106001 | ATTP_4-41106001 | Mittlere Gusen Lungitz | 48.2935 | 14.4759 | 7700 | 6857 | NO | 42.8562 | 0 | 0 | 0 | 248.5662 | 1491.3975 | AT31 | C
AT | AT315 | ATAG_4-41726001 | ATTP_4-41726001 | Pöndorf | 47.9871 | 13.3851 | 7850 | 7314 | NO | 45.7125 | 0 | 0 | 0 | 265.1325 | 1590.795 | AT31 | A
AT | AT311 | ATAG_4-41204001 | ATTP_4-41204001 | Eberschwang | 48.1671 | 13.5579 | 8000 | 4943 | NO | 30.8938 | 0 | 0 | 0 | 179.1837 | 1075.1025 | AT31 | B
AT | AT311 | ATAG_4-40422002 | ATTP_4-40422002 | Mauerkirchen | 48.1977 | 13.1248 | 8000 | 5657 | NO | 35.3563 | 0 | 0 | 0 | 205.0662 | 1230.3975 | AT31 | A
AT | AT314 | ATAG_4-40909001 | ATTP_4-40909001 | Molln | 47.8941 | 14.2553 | 8000 | 4233 | NO | 26.4563 | 0 | 0 | 0 | 153.4462 | 920.6775 | AT31 | A
AT | AT311 | ATAG_4-41426001 | ATTP_4-41426001 | Pram-Pfudabach | 48.4126 | 13.52 | 8000 | 5284 | NO | 33.025 | 0 | 0 | 0 | 191.545 | 1149.27 | AT31 | A
AT | AT314 | ATAG_4-41505001 | ATTP_4-41505001 | Gaflenztal | 47.8527 | 14.6432 | 8200 | 5400 | NO | 33.75 | 0 | 0 | 0 | 195.75 | 1174.5 | AT31 | A
AT | AT314 | ATAG_4-40903001 | ATTP_4-40903001 | Hinterstoder | 47.7088 | 14.1651 | 9000 | 4220 | NO | 26.375 | 0 | 0 | 0 | 152.975 | 917.85 | AT31 | B
AT | AT313 | ATAG_4-41303001 | ATTP_4-41303001 | Aigen-Schlögl | 48.6328 | 13.9749 | 9000 | 5415 | NO | 33.8438 | 0 | 0 | 0 | 196.2937 | 1177.7625 | AT31 | B
AT | AT311 | ATAG_4-40402001 | ATTP_4-40402001 | Aspach | 48.1903 | 13.3009 | 9500 | 7160 | NO | 44.75 | 0 | 0 | 0 | 259.55 | 1557.3 | AT31 | A
AT | AT311 | ATAG_4-41430001 | ATTP_4-41430001 | Mittleres Pramtal | 48.3195 | 13.6295 | 9500 | 10104 | NO | 63.15 | 0 | 0 | 0 | 366.27 | 2197.62 | AT31 | A
AT | AT311 | ATAG_4-40406001 | ATTP_4-40406001 | Eggelsberg | 48.0705 | 12.9807 | 9522 | 5157 | NO | 32.2313 | 0 | 0 | 0 | 186.9412 | 1121.6475 | AT31 | B
AT | AT311 | ATAG_4-40428001 | ATTP_4-40428001 | Salzach-Mitte | 48.0439 | 12.8249 | 10000 | 7028 | NO | 43.925 | 0 | 0 | 0 | 254.765 | 1528.59 | AT31 | A
AT | AT313 | ATAG_4-41603002 | ATTP_4-41603002 | Bad Leonfelden | 48.4942 | 14.3013 | 10000 | 10183 | NO | 63.6438 | 0 | 0 | 0 | 369.1338 | 2214.8025 | AT31 | C
CZ | CZ020 |  | CZ2101-772399-00232904-4/1U | COV Tynec nad Sazavou | 49.8344 | 14.5826 | 6600 | 2862 | NO | 17.8875 | 0 | 0 | 0 | 103.7475 | 622.485 | CZ02 | A
CZ | CZ020 |  | CZ2102-602868-46356975-4/1U | COV Beroun | 49.9586 | 14.0939 | 35783 | 28160 | NO | 176 | 0 | 0 | 0 | 1020.8 | 6124.8 | CZ02 | B
CZ | CZ020 |  | CZ2103-609170-00240079-4/1U | COV Brandys nad Labem - Stara Boleslav | 50.1936 | 14.6623 | 20000 | 10900 | NO | 68.125 | 0 | 0 | 0 | 395.125 | 2370.75 | CZ02 | B
CZ | CZ020 |  | CZ2103-619159-00240117-4/1U | COV Celakovice | 50.1692 | 14.7357 | 10475 | 8381 | NO | 52.3813 | 0 | 0 | 0 | 303.8112 | 1822.8675 | CZ02 | B
CZ | CZ020 |  | CZ2103-702404-00240524-4/1U | COV Nehvizdy | 50.1361 | 14.7373 | 6000 | 2465 | NO | 15.4062 | 0 | 0 | 0 | 89.3563 | 536.1375 | CZ02 | B
CZ | CZ020 |  | CZ2103-708992-00240559-4/1U | COV Odolena Voda | 50.2402 | 14.4135 | 6000 | 4931 | NO | 30.8187 | 0 | 0 | 0 | 178.7487 | 1072.4925 | CZ02 | B
CZ | CZ020 |  | CZ2103-775738-00240931-4/1U | COV Uvaly | 50.0829 | 14.7197 | 6048 | 4192 | NO | 26.2 | 0 | 0 | 0 | 151.96 | 911.76 | CZ02 | A
CZ | CZ020 |  | CZ2104-618349-46356967-4/1U | COV Caslav | 49.9251 | 15.395 | 15000 | 8157 | NO | 50.9812 | 0 | 0 | 0 | 295.6912 | 1774.1475 | CZ02 | A
CZ | CZ020 |  | CZ2105-620386-00241121-4/1U | COV Cernosice | 49.9661 | 14.3297 | 7500 | 5891 | NO | 36.8188 | 0 | 0 | 0 | 213.5487 | 1281.2925 | CZ02 | A
CZ | CZ020 |  | CZ2105-627810-00241181-4/1U | COV Dobrichovice | 49.9322 | 14.2887 | 7333 | 11766 | NO | 73.5375 | 0 | 0 | 0 | 426.5175 | 2559.105 | CZ02 | A
CZ | CZ020 |  | CZ2105-645834-00241237-4/1U | COV Hostivice | 50.0788 | 14.2664 | 9670 | 8110 | NO | 50.6875 | 0 | 0 | 0 | 293.9875 | 1763.925 | CZ02 | A
CZ | CZ020 |  | CZ2105-655465-00241296-4/1U | COV Chyne | 50.065 | 14.2369 | 6000 | 3138 | NO | 19.6125 | 0 | 0 | 0 | 113.7525 | 682.515 | CZ02 | A
CZ | CZ020 |  | CZ2105-658618-00241318-4/1U | COV Jesenice | 49.9726 | 14.514 | 7500 | 5504 | NO | 34.4 | 0 | 0 | 0 | 199.52 | 1197.12 | CZ02 | A
CZ | CZ020 |  | CZ2105-660094-00241326-4/1U | COV Jilove u Prahy | 49.889 | 14.497 | 6500 | 4645 | NO | 29.0312 | 0 | 0 | 0 | 168.3812 | 1010.2875 | CZ02 | B
CZ | CZ020 |  | CZ2105-697621-00242748-4/1U | COV Mnisek pod Brdy | 49.8699 | 14.2785 | 6000 | 7927 | NO | 49.5437 | 0 | 0 | 0 | 287.3537 | 1724.1225 | CZ02 | A
CZ | CZ020 |  | CZ2105-733962-00241563-4/1U | COV Pruhonice | 50.0158 | 14.5539 | 7000 | 4573 | NO | 28.5813 | 0 | 0 | 0 | 165.7712 | 994.6275 | CZ01 | A
CZ | CZ020 |  | CZ2105-736422-00241580-4/1U | COV Psary | 49.9356 | 14.5098 | 6000 | 5549 | NO | 34.6812 | 0 | 0 | 0 | 201.1513 | 1206.9075 | CZ02 | A
CZ | CZ020 |  | CZ2105-742503-00241610-4/1U | COV Roztoky u Prahy | 50.1586 | 14.4003 | 20000 | 12740 | NO | 79.625 | 0 | 0 | 0 | 461.825 | 2770.95 | CZ02 | A
CZ | CZ020 |  | CZ2105-743313-00233773-4/1U | COV Rudna - Horelice | 50.0229 | 14.2179 | 9200 | 5249 | NO | 32.8062 | 0 | 0 | 0 | 190.2762 | 1141.6575 | CZ02 | A
CZ | CZ020 |  | CZ2105-781029-00507644-4/1U | COV Vestec | 49.99 | 14.5 | 7340 | 6575 | NO | 41.0938 | 0 | 0 | 0 | 238.3437 | 1430.0625 | CZ02 | B
CZ | CZ020 |  | CZ2106-622826-00235334-4/1U | COV Cesky Brod | 50.0805 | 14.8854 | 9461 | 8718 | NO | 54.4875 | 0 | 0 | 0 | 316.0275 | 1896.165 | CZ02 | B
CZ | CZ020 |  | CZ2107-627968-00242098-4/1U | COV Dobris | 49.7839 | 14.1882 | 13000 | 8844 | NO | 55.275 | 0 | 0 | 0 | 320.595 | 1923.57 | CZ02 | B
CZ | CZ020 |  | CZ2108-645371-46356975-4/1U | COV Horovice | 49.8474 | 13.9138 | 20000 | 6621 | NO | 41.3813 | 0 | 0 | 0 | 240.0112 | 1440.0675 | CZ02 | B
CZ | CZ020 |  | CZ2109-665177-46356991-4/1U | COV Kladno - Vrapice | 50.1669 | 14.1741 | 86333 | 97839 | YES | 611.4937 | 1956.78 | 1467.585 | 2935.17 | 3546.6637 | 21279.9825 | CZ02 | C
CZ | CZ020 |  | CZ2109-755567-46356991-4/1U | COV Stochov | 50.1377 | 13.9682 | 5250 | 5420 | NO | 33.875 | 0 | 0 | 0 | 196.475 | 1178.85 | CZ02 | A
CZ | CZ020 |  | CZ2109-764558-00234516-4/1U | COV Kladno - Svermov | 50.1721 | 14.1244 | 6616 | 5498 | NO | 34.3625 | 0 | 0 | 0 | 199.3025 | 1195.815 | CZ02 | B
CZ | CZ051 |  | CZ5105-647390-49099469-4/1U | COV Hradek nad Nisou | 50.8549 | 14.8325 | 7854 | 7400 | NO | 46.25 | 0 | 0 | 0 | 268.25 | 1609.5 | CZ05 | B
CZ | CZ051 |  | CZ5105-682209-49099469-4/1U | COV Liberec | 50.7809 | 15.0328 | 190333 | 187089 | YES | 1169.3063 | 3741.78 | 2806.335 | 5612.67 | 6781.9762 | 40691.8575 | CZ05 | A
CZ | CZ051 |  | CZ5106-707155-49099469-4/1U | COV Novy Bor | 50.7503 | 14.5403 | 13400 | 7975 | NO | 49.8438 | 0 | 0 | 0 | 289.0938 | 1734.5625 | CZ05 | B
CZ | CZ051 |  | CZ5107-686751-49295934-4/1U | COV Lomnice nad Popelkou | 50.5258 | 15.3866 | 5500 | 5318 | NO | 33.2375 | 0 | 0 | 0 | 192.7775 | 1156.665 | CZ05 | B
CZ | CZ051 |  | CZ5107-747271-00276111-4/1U | COV Semily | 50.6147 | 15.316 | 13333 | 6317 | NO | 39.4813 | 0 | 0 | 0 | 228.9913 | 1373.9475 | CZ05 | A
CZ | CZ051 |  | CZ5108-778753-49099469-4/2U | COV Tanvald | 50.7325 | 15.3142 | 9037 | 3575 | NO | 22.3438 | 0 | 0 | 0 | 129.5938 | 777.5625 | CZ05 | B
CZ | CZ051 |  | CZ5109-771601-49295934-4/1U | COV Turnov | 50.5798 | 15.1478 | 20000 | 16309 | NO | 101.9312 | 0 | 0 | 0 | 591.2012 | 3547.2075 | CZ05 | A
CZ | CZ051 |  | CZ5110-796221-49099469-4/1U | COV zelezny Brod | 50.6403 | 15.243 | 7566 | 2109 | NO | 13.1813 | 0 | 0 | 0 | 76.4512 | 458.7075 | CZ05 | A
CZ | CZ052 |  | CZ5201-612766-00272523-4/1U | COV Broumov | 50.5697 | 16.343 | 25167 | 11550 | NO | 72.1875 | 0 | 0 | 0 | 418.6875 | 2512.125 | CZ05 | B
CZ | CZ052 |  | CZ5202-627534-00274879-4/1U | COV Dobruska | 50.2962 | 16.1249 | 10000 | 26871 | NO | 167.9437 | 0 | 0 | 0 | 974.0737 | 5844.4425 | CZ05 | A
CZ | CZ052 |  | CZ5202-711951-00275191-4/1U | COV Opocno | 50.269 | 16.0826 | 8200 | 4642 | NO | 29.0125 | 0 | 0 | 0 | 168.2725 | 1009.635 | CZ05 | C
CZ | CZ052 |  | CZ5203-633968-26891395-4/1U | COV Dvur Kralove nad Labem | 50.4239 | 15.8207 | 88000 | 12760 | YES | 79.75 | 255.2 | 191.4 | 382.8 | 462.55 | 2775.3 | CZ05 | A
CZ | CZ052 |  | CZ5204-645168-60109149-4/1U | COV Horice | 50.3549 | 15.6259 | 16700 | 8641 | NO | 54.0063 | 0 | 0 | 0 | 313.2362 | 1879.4175 | CZ05 | B
CZ | CZ052 |  | CZ5205-651800-48172898-4/1U | COV Chlumec nad Cidlinou | 50.1467 | 15.4612 | 5496 | 3903 | NO | 24.3938 | 0 | 0 | 0 | 141.4837 | 848.9025 | CZ05 | B
CZ | CZ052 |  | CZ5205-726583-48172898-4/1U | COV Hradec Kralove | 50.179 | 15.8164 | 141666 | 96899 | YES | 605.6187 | 1937.98 | 1453.485 | 2906.97 | 3512.5887 | 21075.5325 | CZ05 | A
CZ | CZ052 |  | CZ5206-657336-00272728-4/1U | COV Jaromer | 50.337 | 15.9111 | 35000 | 8290 | NO | 51.8125 | 0 | 0 | 0 | 300.5125 | 1803.075 | CZ05 | B
CZ | CZ052 |  | CZ5207-659541-60109149-4/1U | COV Jicin | 50.4201 | 15.3568 | 35000 | 25004 | YES | 156.275 | 500.08 | 375.06 | 750.12 | 906.395 | 5438.37 | CZ05 | A
CZ | CZ020 |  | CZ2118-745928-46357009-4/1U | COV Sadska | 50.1528 | 14.9767 | 5066 | 2247 | NO | 14.0438 | 0 | 0 | 0 | 81.4537 | 488.7225 | CZ02 | C
CZ | CZ020 |  | CZ2119-693286-46357009-4/1U | COV Mestec Kralove | 50.2031 | 15.2814 | 5200 | 2712 | NO | 16.95 | 0 | 0 | 0 | 98.31 | 589.86 | CZ02 | A
CZ | CZ020 |  | CZ2119-723495-00239640-4/1U | COV Podebrady | 50.1546 | 15.1079 | 25000 | 60886 | YES | 380.5375 | 1217.72 | 913.29 | 1826.58 | 2207.1175 | 13242.705 | CZ02 | A
CZ | CZ020 |  | CZ2120-614271-00242004-4/1U | COV Breznice | 49.5477 | 13.9688 | 8500 | 3918 | NO | 24.4875 | 0 | 0 | 0 | 142.0275 | 852.165 | CZ02 | C
CZ | CZ020 |  | CZ2120-735426-00243132-4/1U | COV Pribram | 49.7052 | 14.0088 | 76300 | 37353 | YES | 233.4562 | 747.06 | 560.295 | 1120.59 | 1354.0462 | 8124.2775 | CZ02 | A
CZ | CZ020 |  | CZ2120-742848-00243221-4/1U | COV Rozmital pod TremSinem | 49.5969 | 13.8778 | 6000 | 2502 | NO | 15.6375 | 0 | 0 | 0 | 90.6975 | 544.185 | CZ02 | A
CZ | CZ020 |  | CZ2121-706744-00244155-4/1U | COV Nove Straseci | 50.1529 | 13.9114 | 5500 | 4371 | NO | 27.3187 | 0 | 0 | 0 | 158.4487 | 950.6925 | CZ02 | A
CZ | CZ020 |  | CZ2121-739081-47019549-4/1U | COV Rakovnik | 50.0933 | 13.7504 | 23000 | 29329 | NO | 183.3063 | 0 | 0 | 0 | 1063.1762 | 6379.0575 | CZ02 | A
CZ | CZ020 |  | CZ2122-745456-00240702-4/1U | COV Ricany u Prahy | 50.0052 | 14.6437 | 16158 | 14171 | NO | 88.5688 | 0 | 0 | 0 | 513.6988 | 3082.1925 | CZ02 | B
CZ | CZ020 |  | CZ2122-779342-45357366-4/1U | COV Velke Popovice - centralni | 49.915 | 14.6411 | 945000 | 45281 | NO | 283.0063 | 0 | 0 | 0 | 1641.4363 | 9848.6175 | CZ02 | B
CZ | CZ020 |  | CZ2123-746533-00243272-4/1U | COV SedlCany | 49.6749 | 14.4299 | 23000 | 17109 | YES | 106.9312 | 342.18 | 256.635 | 513.27 | 620.2012 | 3721.2075 | CZ02 | C
CZ | CZ020 |  | CZ2124-749362-00234877-4/1U | COV Slany - Blahotice | 50.234 | 14.1096 | 19083 | 9417 | NO | 58.8562 | 0 | 0 | 0 | 341.3662 | 2048.1975 | CZ02 | B
CZ | CZ020 |  | CZ2125-783544-00232947-4/1U | COV Vlasim | 49.714 | 14.9068 | 12900 | 15992 | NO | 99.95 | 0 | 0 | 0 | 579.71 | 3478.26 | CZ02 | A
CZ | CZ020 |  | CZ2126-785041-00232963-4/1U | COV Votice | 49.6533 | 14.6324 | 5500 | 10515 | NO | 65.7188 | 0 | 0 | 0 | 381.1687 | 2287.0125 | CZ02 | C
CZ | CZ031 |  | CZ3101-605247-00250996-4/1U | COV Blatna | 49.4147 | 13.902 | 7500 | 3742 | NO | 23.3875 | 0 | 0 | 0 | 135.6475 | 813.885 | CZ03 | C
CZ | CZ031 |  | CZ3102-648001-00244732-4/1U | COV Ceske Budejovice | 49.0154 | 14.4573 | 375000 | 139536 | YES | 872.1 | 2790.72 | 2093.04 | 4186.08 | 5058.18 | 30349.08 | CZ03 | A
CZ | CZ031 |  | CZ3103-622931-28160363-4/1U | COV Cesky Krumlov | 48.781 | 14.2972 | 460000 | 40261 | YES | 251.6313 | 805.22 | 603.915 | 1207.83 | 1459.4612 | 8756.7675 | CZ03 | A
CZ | CZ031 |  | CZ3103-643700-00245895-4/2U | COV Horni Plana | 48.761 | 14.0303 | 6600 | 2416 | NO | 15.1 | 0 | 0 | 0 | 87.58 | 525.48 | CZ03 | A
CZ | CZ031 |  | CZ3104-624403-00246476-4/1U | COV Dacice | 49.073 | 15.4215 | 9400 | 3974 | NO | 24.8375 | 0 | 0 | 0 | 144.0575 | 864.345 | CZ03 | B
CZ | CZ031 |  | CZ3104-758191-00247545-4/1U | COV Studena | 49.1903 | 15.2903 | 5200 | 4516 | NO | 28.225 | 0 | 0 | 0 | 163.705 | 982.23 | CZ03 | A
CZ | CZ031 |  | CZ3105-660523-00246875-4/1U | COV Jindrichuv Hradec | 49.1283 | 15.0112 | 87500 | 56529 | YES | 353.3063 | 1130.58 | 847.935 | 1695.87 | 2049.1762 | 12295.0575 | CZ03 | A
CZ | CZ031 |  | CZ3106-663140-00245941-4/1U | COV Kaplice | 48.729 | 14.5057 | 12650 | 11501 | NO | 71.8813 | 0 | 0 | 0 | 416.9112 | 2501.4675 | CZ03 | B
CZ | CZ031 |  | CZ3106-777854-00246174-4/1U | COV Velesin - stabilizacni nadrz | 48.8285 | 14.4717 | 6200 | 2482 | NO | 15.5125 | 0 | 0 | 0 | 89.9725 | 539.835 | CZ03 | B
CZ | CZ031 |  | CZ3107-694673-00249831-4/1U | COV Milevsko | 49.4394 | 14.3915 | 14500 | 4644 | NO | 29.025 | 0 | 0 | 0 | 168.345 | 1010.07 | CZ03 | A
CZ | CZ031 |  | CZ3108-720755-00249998-4/1U | COV Pisek | 49.3192 | 14.1532 | 62833 | 36145 | YES | 225.9062 | 722.9 | 542.175 | 1084.35 | 1310.2562 | 7861.5375 | CZ03 | A
CZ | CZ031 |  | CZ3108-733857-00250023-4/1U | COV Protivin | 49.2054 | 14.2195 | 49200 | 22809 | NO | 142.5563 | 0 | 0 | 0 | 826.8263 | 4960.9575 | CZ03 | A
CZ | CZ031 |  | CZ3109-732630-00250627-4/1U | COV Prachatice | 49.0218 | 14.0123 | 33000 | 7847 | YES | 49.0437 | 156.94 | 117.705 | 235.41 | 284.4537 | 1706.7225 | CZ03 | A
CZ | CZ031 |  | CZ3109-784737-00250830-4/1U | COV Volary | 48.9171 | 13.8902 | 7200 | 1329 | NO | 8.3063 | 0 | 0 | 0 | 48.1762 | 289.0575 | CZ03 | B
CZ | CZ031 |  | CZ3110-751707-00252921-4/1U | COV Sobeslav | 49.2685 | 14.7001 | 9300 | 4426 | NO | 27.6625 | 0 | 0 | 0 | 160.4425 | 962.655 | CZ03 | B
CZ | CZ031 |  | CZ3110-780685-00253081-4/1U | COV Veseli nad Luznici | 49.2038 | 14.7147 | 15000 | 19815 | NO | 123.8438 | 0 | 0 | 0 | 718.2938 | 4309.7625 | CZ03 | A
CZ | CZ031 |  | CZ3111-755915-00251810-4/1U | COV Strakonice | 49.2631 | 13.9232 | 75000 | 27430 | YES | 171.4375 | 548.6 | 411.45 | 822.9 | 994.3375 | 5966.025 | CZ03 | A
CZ | CZ031 |  | CZ3111-784958-00252000-4/1U | COV Volyne | 49.1744 | 13.8883 | 7500 | 2674 | NO | 16.7125 | 0 | 0 | 0 | 96.9325 | 581.595 | CZ03 | B
CZ | CZ031 |  | CZ3112-601543-00252069-4/1U | COV Bechyne | 49.296 | 14.4745 | 7500 | 4446 | NO | 27.7875 | 0 | 0 | 0 | 161.1675 | 967.005 | CZ03 | A
CZ | CZ031 |  | CZ3112-619418-26069539-4/1U | COV Tabor - ACOV | 49.4003 | 14.6786 | 95000 | 93550 | YES | 584.6875 | 1871 | 1403.25 | 2806.5 | 3391.1875 | 20347.125 | CZ03 | B
CZ | CZ031 |  | CZ3112-666513-26069539-4/1U | COV Tabor - Klokoty | 49.4111 | 14.6388 | 30000 | 14570 | YES | 91.0625 | 291.4 | 218.55 | 437.1 | 528.1625 | 3168.975 | CZ03 | B
CZ | CZ031 |  | CZ3113-607746-00244686-4/1U | COV Borovany | 48.8871 | 14.6411 | 9500 | 1292 | NO | 8.075 | 0 | 0 | 0 | 46.835 | 281.01 | CZ03 | B
CZ | CZ031 |  | CZ3114-615021-00247618-4/1U | COV Trebon | 49.0326 | 14.7554 | 16410 | 21525 | NO | 134.5312 | 0 | 0 | 0 | 780.2812 | 4681.6875 | CZ03 | A
CZ | CZ031 |  | CZ3115-772127-00245585-4/1U | COV Tyn nad Vltavou | 49.2291 | 14.4049 | 6000 | 5031 | NO | 31.4437 | 0 | 0 | 0 | 182.3737 | 1094.2425 | CZ03 | B
CZ | CZ031 |  | CZ3116-782084-00250805-4/1U | COV Vimperk | 49.0652 | 13.7824 | 9800 | 3086 | NO | 19.2875 | 0 | 0 | 0 | 111.8675 | 671.205 | CZ03 | A
CZ | CZ031 |  | CZ3117-784281-00251984-4/1U | COV Vodnany | 49.1421 | 14.1906 | 28500 | 11584 | NO | 72.4 | 0 | 0 | 0 | 419.92 | 2519.52 | CZ03 | A
CZ | CZ032 |  | CZ3202-630853-00253316-4/1U | COV Domazlice | 49.4322 | 12.9605 | 34000 | 16605 | YES | 103.7812 | 332.1 | 249.075 | 498.15 | 601.9312 | 3611.5875 | CZ03 | A
CZ | CZ032 |  | CZ3202-732851-00253464-4/1U | COV Kdyne - jih | 49.3891 | 13.0267 | 5000 | 3904 | NO | 24.4 | 0 | 0 | 0 | 141.52 | 849.12 | CZ03 | B
CZ | CZ032 |  | CZ3203-641855-00255513-4/1U | COV Horazdovice | 49.3178 | 13.719 | 9500 | 2919 | NO | 18.2438 | 0 | 0 | 0 | 105.8138 | 634.8825 | CZ03 | A
CZ | CZ032 |  | CZ3204-644871-00253383-4/1U | COV Horsovsky Tyn | 49.5329 | 12.9615 | 11818 | 3942 | NO | 24.6375 | 0 | 0 | 0 | 142.8975 | 857.385 | CZ03 | B
CZ | CZ032 |  | CZ3205-665797-00255661-4/1U | COV Klatovy | 49.4117 | 13.2693 | 100000 | 83516 | YES | 521.975 | 1670.32 | 1252.74 | 2505.48 | 3027.455 | 18164.73 | CZ03 | A
CZ | CZ032 |  | CZ3205-708453-00255921-4/1U | COV Nyrsko | 49.3005 | 13.1492 | 8000 | 4767 | NO | 29.7938 | 0 | 0 | 0 | 172.8037 | 1036.8225 | CZ03 | B
CZ | CZ032 |  | CZ3206-672645-00257966-4/1U | COV Kralovice | 49.9789 | 13.492 | 9900 | 3873 | NO | 24.2063 | 0 | 0 | 0 | 140.3962 | 842.3775 | CZ03 | A
CZ | CZ032 |  | CZ3207-703478-00256986-4/1U | COV Nepomuk | 49.4928 | 13.581 | 7500 | 1768 | NO | 11.05 | 0 | 0 | 0 | 64.09 | 384.54 | CZ03 | B
CZ | CZ064 |  | CZ6204-723835-49455168-4/1U | COV Podivin | 48.8232 | 16.852 | 5250 | 2807 | NO | 17.5437 | 0 | 0 | 0 | 101.7537 | 610.5225 | CZ06 | A
CZ | CZ064 |  | CZ6204-776696-49455168-4/1U | COV Valtice | 48.7485 | 16.751 | 9700 | 5545 | NO | 34.6562 | 0 | 0 | 0 | 201.0062 | 1206.0375 | CZ06 | A
CZ | CZ064 |  | CZ6204-778672-00283673-4/1U | COV Velke Bilovice | 48.8558 | 16.8776 | 8000 | 4716 | NO | 29.475 | 0 | 0 | 0 | 170.955 | 1025.73 | CZ06 | A
CZ | CZ064 |  | CZ6205-615161-49454587-4/1U | COV Bucovice | 49.1516 | 16.9824 | 9860 | 19183 | NO | 119.8938 | 0 | 0 | 0 | 695.3837 | 4172.3025 | CZ06 | A
CZ | CZ064 |  | CZ6206-633585-00284882-4/1U | COV Dubnany | 48.9136 | 17.086 | 6500 | 5237 | NO | 32.7313 | 0 | 0 | 0 | 189.8413 | 1139.0475 | CZ06 | A
CZ | CZ032 |  | CZ3208-683850-00258059-4/1U | COV Line | 49.699 | 13.2661 | 5475 | 3477 | NO | 21.7312 | 0 | 0 | 0 | 126.0412 | 756.2475 | CZ03 | B
CZ | CZ032 |  | CZ3208-767557-49745221-4/1U | COV Sdruzeni obci Tlucna. Vejprnice. Nyrany | 49.726 | 13.2527 | 9900 | 9485 | NO | 59.2812 | 0 | 0 | 0 | 343.8313 | 2062.9875 | CZ03 | A
CZ | CZ032 |  | CZ3209-721981-00075370-4/1U | COV Plzen | 49.7646 | 13.4063 | 427917 | 352374 | YES | 2202.3375 | 7047.48 | 5285.61 | 10571.22 | 12773.5575 | 76641.345 | CZ03 | A
CZ | CZ032 |  | CZ3209-755150-00257257-4/1U | COV Stary Plzenec - II centralni | 49.6985 | 13.4797 | 8000 | 9308 | NO | 58.175 | 0 | 0 | 0 | 337.415 | 2024.49 | CZ03 | A
CZ | CZ032 |  | CZ3210-735256-00257125-4/1U | COV Prestice | 49.5753 | 13.3457 | 8200 | 4781 | NO | 29.8812 | 0 | 0 | 0 | 173.3112 | 1039.8675 | CZ03 | B
CZ | CZ032 |  | CZ3211-740691-00259047-4/1U | COV Rokycany | 49.7456 | 13.5809 | 25000 | 8915 | YES | 55.7188 | 178.3 | 133.725 | 267.45 | 323.1687 | 1939.0125 | CZ03 | A
CZ | CZ032 |  | CZ3212-627615-00256552-4/1U | COV Dobrany | 49.6609 | 13.2979 | 9600 | 4686 | NO | 29.2875 | 0 | 0 | 0 | 169.8675 | 1019.205 | CZ03 | B
CZ | CZ032 |  | CZ3212-641553-00253367-4/1U | COV Holysov | 49.5999 | 13.0968 | 7000 | 3679 | NO | 22.9938 | 0 | 0 | 0 | 133.3638 | 800.1825 | CZ03 | A
CZ | CZ032 |  | CZ3212-755516-00257265-4/1U | COV Stod | 49.6418 | 13.1715 | 5000 | 4550 | NO | 28.4375 | 0 | 0 | 0 | 164.9375 | 989.625 | CZ03 | A
CZ | CZ032 |  | CZ3213-757837-47700521-4/1U | COV Stribro | 49.7507 | 13.0066 | 15500 | 18398 | NO | 114.9875 | 0 | 0 | 0 | 666.9275 | 4001.565 | CZ03 | A
CZ | CZ032 |  | CZ3214-759601-00256129-4/1U | COV Susice | 49.2531 | 13.5521 | 13500 | 12934 | NO | 80.8375 | 0 | 0 | 0 | 468.8575 | 2813.145 | CZ03 | A
CZ | CZ032 |  | CZ3215-652211-47700521-4/1U | COV Chodova Plana | 49.8914 | 12.7202 | 13700 | 4633 | NO | 28.9563 | 0 | 0 | 0 | 167.9462 | 1007.6775 | CZ03 | B
CZ | CZ032 |  | CZ3215-721280-00260096-4/1U | COV Plana | 49.8607 | 12.7403 | 5950 | 3421 | NO | 21.3812 | 0 | 0 | 0 | 124.0112 | 744.0675 | CZ03 | A
CZ | CZ032 |  | CZ3215-764914-47700521-4/1U | COV Tachov | 49.7942 | 12.6558 | 11578 | 21352 | NO | 133.45 | 0 | 0 | 0 | 774.01 | 4644.06 | CZ03 | A
CZ | CZ041 |  | CZ4101-600521-49787977-4/1U | COV As | 50.2377 | 12.1864 | 25000 | 22419 | NO | 140.1188 | 0 | 0 | 0 | 812.6887 | 4876.1325 | CZ04 | C
CZ | CZ041 |  | CZ4102-651028-49787977-4/1U | COV Cheb | 50.0869 | 12.3917 | 65000 | 32589 | YES | 203.6813 | 651.78 | 488.835 | 977.67 | 1181.3512 | 7088.1075 | CZ04 | A
CZ | CZ041 |  | CZ4103-634522-00254801-4/1U | COV Nejdek | 50.3079 | 12.7547 | 8150 | 8820 | NOT KNOWN | 55.125 | 0 | 0 | 0 | 319.725 | 1918.35 | CZ04 | B
CZ | CZ041 |  | CZ4103-663701-47700521-4/1U | COV Karlovy Vary - Drahonovice | 50.2394 | 12.8979 | 80000 | 58895 | YES | 368.0938 | 1177.9 | 883.425 | 1766.85 | 2134.9437 | 12809.6625 | CZ04 | A
CZ | CZ041 |  | CZ4103-705250-47700521-4/1U | COV Nova Role | 50.2707 | 12.7922 | 5000 | 3755 | NO | 23.4688 | 0 | 0 | 0 | 136.1188 | 816.7125 | CZ04 | A
CZ | CZ041 |  | CZ4104-673293-25241800-4/1U | COV Kraslice | 50.314 | 12.521 | 12000 | 3451 | NO | 21.5687 | 0 | 0 | 0 | 125.0987 | 750.5925 | CZ04 | A
CZ | CZ041 |  | CZ4104-741531-00259551-4/1U | COV Rotava | 50.315 | 12.5649 | 5000 | 1822 | NO | 11.3875 | 0 | 0 | 0 | 66.0475 | 396.285 | CZ04 | C
CZ | CZ041 |  | CZ4105-765961-47700521-4/1U | COV Tepla | 49.9797 | 12.858 | 5000 | 1245 | NO | 7.7812 | 0 | 0 | 0 | 45.1312 | 270.7875 | CZ04 | B
CZ | CZ041 |  | CZ4105-901903-49787977-4/1U | COV Marianske Lazne | 49.9351 | 12.7253 | 16807 | 20304 | NO | 126.9 | 0 | 0 | 0 | 736.02 | 4416.12 | CZ04 | C
CZ | CZ041 |  | CZ4106-656437-47700521-4/1U | COV Jachymov | 50.3547 | 12.9326 | 11400 | 5810 | NO | 36.3125 | 0 | 0 | 0 | 210.6125 | 1263.675 | CZ04 | B
CZ | CZ041 |  | CZ4106-715883-47700521-4/1U | COV Ostrov | 50.3033 | 12.9661 | 21652 | 15054 | NO | 94.0875 | 0 | 0 | 0 | 545.7075 | 3274.245 | CZ04 | A
CZ | CZ041 |  | CZ4107-636339-49163451-4/1U | COV Habartov a Bukovany | 50.1742 | 12.5576 | 5600 | 2961 | NO | 18.5063 | 0 | 0 | 0 | 107.3363 | 644.0175 | CZ04 | C
CZ | CZ041 |  | CZ4107-644056-47700521-4/1U | COV Horni Slavkov | 50.1429 | 12.8005 | 9350 | 8014 | NO | 50.0875 | 0 | 0 | 0 | 290.5075 | 1743.045 | CZ04 | A
CZ | CZ041 |  | CZ4107-652172-47700521-4/1U | COV Chodov | 50.2363 | 12.7518 | 14697 | 15381 | NO | 96.1313 | 0 | 0 | 0 | 557.5613 | 3345.3675 | CZ04 | A
CZ | CZ041 |  | CZ4107-752223-00259586-4/1U | COV Sokolov | 50.1819 | 12.6711 | 33000 | 16165 | YES | 101.0312 | 323.3 | 242.475 | 484.95 | 585.9812 | 3515.8875 | CZ04 | A
CZ | CZ020 |  | CZ2115-602124-46356983-4/1U | COV Benatky nad Jizerou | 50.2852 | 14.8174 | 9900 | 6620 | NO | 41.375 | 0 | 0 | 0 | 239.975 | 1439.85 | CZ02 | A
CZ | CZ020 |  | CZ2115-696641-46356983-4/1U | COV Mlada Boleslav - Neuberk | 50.4236 | 14.8946 | 40000 | 36713 | YES | 229.4562 | 734.26 | 550.695 | 1101.39 | 1330.8462 | 7985.0775 | CZ02 | A
CZ | CZ020 |  | CZ2115-900125-46356983-4/1U | COV Mlada Boleslav - Podlazky | 50.4244 | 14.8941 | 50367 | 35668 | YES | 222.925 | 713.36 | 535.02 | 1070.04 | 1292.965 | 7757.79 | CZ02 | A
CZ | CZ020 |  | CZ2116-697575-46356983-4/1U | COV Mnichovo HradiSte | 50.5105 | 14.965 | 7040 | 5523 | NO | 34.5188 | 0 | 0 | 0 | 200.2088 | 1201.2525 | CZ02 | A
CZ | CZ020 |  | CZ2117-703567-45147787-4/1U | COV Neratovice Spolana | 50.2799 | 14.5228 | 150000 | 82785 | NO | 517.4062 | 0 | 0 | 0 | 3000.9562 | 18005.7375 | CZ02 | A
CZ | CZ020 |  | CZ2118-708232-00239500-4/1U | COV Nymburk | 50.1775 | 15.0326 | 25000 | 40333 | NO | 252.0812 | 0 | 0 | 0 | 1462.0712 | 8772.4275 | CZ02 | A
CZ | CZ053 |  | CZ5303-641146-60108631-4/1U | COV Holice | 50.073 | 15.9768 | 9500 | 4301 | NO | 26.8812 | 0 | 0 | 0 | 155.9112 | 935.4675 | CZ05 | A
CZ | CZ053 |  | CZ5304-638731-48171590-4/1U | COV Hermanuv Mestec | 49.959 | 15.6796 | 5000 | 3546 | NO | 22.1625 | 0 | 0 | 0 | 128.5425 | 771.255 | CZ05 | B
CZ | CZ053 |  | CZ5304-653799-48171590-4/1U | COV Chrast | 49.9093 | 15.9457 | 18216 | 3054 | NO | 19.0875 | 0 | 0 | 0 | 110.7075 | 664.245 | CZ05 | B
CZ | CZ053 |  | CZ5304-654299-48171590-4/1U | COV Chrudim | 49.9651 | 15.808 | 50000 | 22715 | YES | 141.9688 | 454.3 | 340.725 | 681.45 | 823.4187 | 4940.5125 | CZ05 | A
CZ | CZ053 |  | CZ5304-749168-00270903-4/1U | COV Skutec | 49.8498 | 15.9895 | 5370 | 3692 | NO | 23.075 | 0 | 0 | 0 | 133.835 | 803.01 | CZ05 | B
CZ | CZ053 |  | CZ5304-770736-48171590-4/1U | COV Tremosnice | 49.8695 | 15.5918 | 5083 | 5307 | NO | 33.1688 | 0 | 0 | 0 | 192.3787 | 1154.2725 | CZ05 | B
CZ | CZ053 |  | CZ5305-620807-00278637-4/1U | COV Mlynice u Cerevene Vody | 50.014 | 16.7453 | 26135 | 7756 | NO | 48.475 | 0 | 0 | 0 | 281.155 | 1686.93 | CZ05 | A
CZ | CZ053 |  | CZ5306-678929-48173398-4/1U | COV Lanskroun | 49.9024 | 16.6251 | 17750 | 12964 | NO | 81.025 | 0 | 0 | 0 | 469.945 | 2819.67 | CZ05 | A
CZ | CZ053 |  | CZ5307-685747-00276944-4/1U | COV Litomysl | 49.8825 | 16.2905 | 28000 | 13258 | YES | 82.8625 | 265.16 | 198.87 | 397.74 | 480.6025 | 2883.615 | CZ05 | A
CZ | CZ053 |  | CZ5308-693341-00276987-4/1U | COV Mestecko Trnavka | 49.7143 | 16.7295 | 11075 | 2015 | NO | 12.5938 | 0 | 0 | 0 | 73.0437 | 438.2625 | CZ05 | B
CZ | CZ053 |  | CZ5308-698806-00277037-4/1U | COV Moravska Trebova | 49.7529 | 16.7171 | 20070 | 10393 | NO | 64.9562 | 0 | 0 | 0 | 376.7462 | 2260.4775 | CZ05 | C
CZ | CZ053 |  | CZ5309-743852-60108631-4/1U | COV Pardubice - Rybitvi - SYNTHESIA | 50.0438 | 15.6956 | 191000 | 111278 | YES | 695.4875 | 2225.56 | 1669.17 | 3338.34 | 4033.8275 | 24202.965 | CZ05 | A
CZ | CZ053 |  | CZ5310-725358-00277177-4/1U | COV Policka | 49.711 | 16.2519 | 28550 | 25991 | NO | 162.4437 | 0 | 0 | 0 | 942.1737 | 5653.0425 | CZ05 | A
CZ | CZ053 |  | CZ5311-734560-60108631-4/1U | COV Prelouc | 50.0439 | 15.5544 | 10500 | 5733 | NO | 35.8313 | 0 | 0 | 0 | 207.8213 | 1246.9275 | CZ05 | B
CZ | CZ053 |  | CZ5312-647233-00277444-4/1U | COV Svitavy | 49.7253 | 16.4767 | 28500 | 21097 | YES | 131.8563 | 421.94 | 316.455 | 632.91 | 764.7663 | 4588.5975 | CZ05 | A
CZ | CZ053 |  | CZ5313-775274-25945793-4/1U | COV Usti nad Orlici | 49.9849 | 16.3886 | 22000 | 12655 | NO | 79.0938 | 0 | 0 | 0 | 458.7437 | 2752.4625 | CZ05 | A
CZ | CZ053 |  | CZ5314-603236-48173398-4/1U | COV Chocen | 50.0089 | 16.2006 | 27666 | 29228 | YES | 182.675 | 584.56 | 438.42 | 876.84 | 1059.515 | 6357.09 | CZ05 | C
CZ | CZ053 |  | CZ5314-788228-00279773-4/1U | COV Vysoke Myto | 49.9699 | 16.1453 | 9950 | 6986 | NO | 43.6625 | 0 | 0 | 0 | 253.2425 | 1519.455 | CZ05 | C
CZ | CZ053 |  | CZ5315-680656-48173398-4/1U | COV Letohrad | 50.03 | 16.4912 | 5000 | 12503 | NO | 78.1437 | 0 | 0 | 0 | 453.2337 | 2719.4025 | CZ05 | A
CZ | CZ063 |  | CZ6101-616958-43383513-4/1U | COV Bystrice nad Pernstejnem | 49.5241 | 16.2758 | 15800 | 7915 | NO | 49.4688 | 0 | 0 | 0 | 286.9187 | 1721.5125 | CZ06 | A
CZ | CZ063 |  | CZ6102-635537-48173002-4/1U | COV Golcuv Jenikov | 49.8331 | 15.471 | 5390 | 2219 | NO | 13.8688 | 0 | 0 | 0 | 80.4387 | 482.6325 | CZ06 | B
CZ | CZ063 |  | CZ6102-637955-48173002-4/1U | COV Perknov | 49.6136 | 15.5425 | 125000 | 75488 | YES | 471.8 | 1509.76 | 1132.32 | 2264.64 | 2736.44 | 16418.64 | CZ06 | A
CZ | CZ063 |  | CZ6103-649325-00248266-4/1U | COV Humpolec | 49.5574 | 15.3617 | 28200 | 24351 | YES | 152.1937 | 487.02 | 365.265 | 730.53 | 882.7237 | 5296.3425 | CZ06 | A
CZ | CZ063 |  | CZ6104-652831-48173002-4/1U | COV Chotebor | 49.726 | 15.6819 | 8000 | 10927 | NO | 68.2938 | 0 | 0 | 0 | 396.1037 | 2376.6225 | CZ06 | B
CZ | CZ063 |  | CZ6105-648698-48460915-4/1U | COV Jihlava | 49.405 | 15.6094 | 99917 | 107301 | YES | 670.6313 | 2146.02 | 1609.515 | 3219.03 | 3889.6612 | 23337.9675 | CZ06 | B
CZ | CZ063 |  | CZ6105-725498-48460915-4/1U | COV Polna | 49.4941 | 15.7119 | 5089 | 4720 | NO | 29.5 | 0 | 0 | 0 | 171.1 | 1026.6 | CZ06 | B
CZ | CZ063 |  | CZ6105-770761-00286753-4/1U | COV Trest | 49.2983 | 15.478 | 6700 | 2923 | NO | 18.2688 | 0 | 0 | 0 | 105.9587 | 635.7525 | CZ06 | A
CZ | CZ063 |  | CZ6106-658227-60418885-4/1U | COV Jemnice | 49.0121 | 15.5724 | 6000 | 3462 | NO | 21.6375 | 0 | 0 | 0 | 125.4975 | 752.985 | CZ06 | A
CZ | CZ063 |  | CZ6106-698903-60418885-4/1U | COV Moravske Budejovice | 49.0615 | 15.8232 | 17600 | 10761 | YES | 67.2563 | 215.22 | 161.415 | 322.83 | 390.0863 | 2340.5175 | CZ06 | B
CZ | CZ042 |  | CZ4201-604348-49099469-4/1U | COV Bilina | 50.5682 | 13.7803 | 19292 | 18909 | NO | 118.1812 | 0 | 0 | 0 | 685.4512 | 4112.7075 | CZ04 | A
CZ | CZ042 |  | CZ4202-607169-49099469-4/1U | COV Decin - Boletice | 50.7436 | 14.1851 | 68000 | 20301 | YES | 126.8813 | 406.02 | 304.515 | 609.03 | 735.9113 | 4415.4675 | CZ04 | A
CZ | CZ042 |  | CZ4202-621293-49099469-4/1U | COV Ceska Kamenice | 50.8005 | 14.3966 | 8000 | 3435 | NO | 21.4688 | 0 | 0 | 0 | 124.5187 | 747.1125 | CZ04 | B
CZ | CZ042 |  | CZ4203-660761-49099469-4/1U | COV Jirkov | 50.5041 | 13.4608 | 40333 | 36919 | YES | 230.7438 | 738.38 | 553.785 | 1107.57 | 1338.3137 | 8029.8825 | CZ04 | A
CZ | CZ042 |  | CZ4203-772615-49099469-4/1U | COV Udlice | 50.4448 | 13.4509 | 50183 | 75023 | YES | 468.8938 | 1500.46 | 1125.345 | 2250.69 | 2719.5837 | 16317.5025 | CZ04 | A
CZ | CZ042 |  | CZ4204-661686-49099469-4/2U | COV Kadan | 50.3703 | 13.2804 | 19250 | 24151 | NO | 150.9437 | 0 | 0 | 0 | 875.4737 | 5252.8425 | CZ04 | A
CZ | CZ042 |  | CZ4204-665657-49099469-4/1U | COV KlaSterec nad Ohri | 50.3771 | 13.1983 | 18330 | 19957 | NO | 124.7313 | 0 | 0 | 0 | 723.4412 | 4340.6475 | CZ04 | B
CZ | CZ042 |  | CZ4204-777579-47700521-4/1U | COV Vejprty | 50.503 | 13.032 | 5067 | 3852 | NO | 24.075 | 0 | 0 | 0 | 139.635 | 837.81 | CZ04 | A
CZ | CZ042 |  | CZ4205-685429-49099469-4/1U | COV Litomerice | 50.5312 | 14.1188 | 97978 | 39589 | YES | 247.4313 | 791.78 | 593.835 | 1187.67 | 1435.1012 | 8610.6075 | CZ04 | A
CZ | CZ042 |  | CZ4205-763691-26161516-4/1U | COV Steti -Papirny Mondi | 50.465 | 14.3669 | 567000 | 295479 | NO | 1846.7437 | 0 | 0 | 0 | 10711.1138 | 64266.6825 | CZ04 | A
CZ | CZ063 |  | CZ6111-679712-48173002-4/1U | COV Ledec nad Sazavou | 49.6997 | 15.2661 | 6600 | 9064 | NO | 56.65 | 0 | 0 | 0 | 328.57 | 1971.42 | CZ06 | A
CZ | CZ063 |  | CZ6111-700185-48173002-4/1U | COV Svetla nad Sazavou | 49.6594 | 15.3749 | 6000 | 7731 | NO | 48.3188 | 0 | 0 | 0 | 280.2487 | 1681.4925 | CZ06 | C
CZ | CZ063 |  | CZ6112-765546-00286745-4/1U | COV Telc | 49.1724 | 15.4624 | 8000 | 7110 | NO | 44.4375 | 0 | 0 | 0 | 257.7375 | 1546.425 | CZ06 | A
CZ | CZ063 |  | CZ6113-657506-60418885-4/1U | COV Jaromerice nad Rokytnou | 49.0913 | 15.9001 | 6965 | 6919 | NO | 43.2437 | 0 | 0 | 0 | 250.8137 | 1504.8825 | CZ06 | B
CZ | CZ080 |  | CZ8119-762342-45193665-4/1U | COV Havirov | 49.785 | 18.3932 | 103183 | 67711 | YES | 423.1937 | 1354.22 | 1015.665 | 2031.33 | 2454.5237 | 14727.1425 | CZ08 | A
CZ | CZ080 |  | CZ8120-744468-00296317-4/1U | COV Rymarov | 49.9296 | 17.2971 | 14000 | 3335 | NO | 20.8438 | 0 | 0 | 0 | 120.8937 | 725.3625 | CZ08 | A
CZ | CZ080 |  | CZ8121-771015-45193665-4/1U | COV Trinec | 49.7127 | 18.6314 | 116250 | 83182 | YES | 519.8875 | 1663.64 | 1247.73 | 2495.46 | 3015.3475 | 18092.085 | CZ08 | C
CZ | CZ080 |  | CZ8122-782998-45193665-4/2U | COV Vitkov | 49.7662 | 17.7637 | 6000 | 3547 | NO | 22.1687 | 0 | 0 | 0 | 128.5787 | 771.4725 | CZ08 | A
CZ | CZ042 |  | CZ4206-629260-49099469-4/1U | COV Litvinov | 50.5517 | 13.5988 | 36000 | 31481 | YES | 196.7563 | 629.62 | 472.215 | 944.43 | 1141.1863 | 6847.1175 | CZ04 | A
CZ | CZ042 |  | CZ4207-687391-49099469-4/1U | COV Louny | 50.3666 | 13.816 | 40000 | 24633 | YES | 153.9563 | 492.66 | 369.495 | 738.99 | 892.9462 | 5357.6775 | CZ04 | A
CZ | CZ042 |  | CZ4207-726117-49099469-4/1U | COV Postoloprty | 50.3592 | 13.7075 | 5000 | 2689 | NO | 16.8063 | 0 | 0 | 0 | 97.4763 | 584.8575 | CZ04 | B
CZ | CZ042 |  | CZ4209-699594-49099469-4/1U | COV Most - Chanov | 50.5067 | 13.6738 | 95000 | 74089 | YES | 463.0563 | 1481.78 | 1111.335 | 2222.67 | 2685.7263 | 16114.3575 | CZ04 | A
CZ | CZ042 |  | CZ4210-675466-49099469-4/1U | COV Kryry | 50.1778 | 13.4338 | 7204 | 1412 | NO | 8.825 | 0 | 0 | 0 | 51.185 | 307.11 | CZ04 | A
CZ | CZ042 |  | CZ4210-723231-49099469-4/1U | COV Podborany | 50.2311 | 13.4144 | 7700 | 7187 | NO | 44.9187 | 0 | 0 | 0 | 260.5287 | 1563.1725 | CZ04 | A
CZ | CZ042 |  | CZ4211-777510-49099469-4/1U | COV Roudnice nad Labem | 50.4313 | 14.2567 | 15120 | 10454 | NO | 65.3375 | 0 | 0 | 0 | 378.9575 | 2273.745 | CZ04 | A
CZ | CZ042 |  | CZ4212-762890-49099469-4/1U | COV Sluknov | 50.9926 | 14.5105 | 7000 | 2307 | NO | 14.4188 | 0 | 0 | 0 | 83.6288 | 501.7725 | CZ04 | C
CZ | CZ042 |  | CZ4213-616702-49099469-4/1U | COV Bystrany | 50.6236 | 13.8691 | 104185 | 73553 | YES | 459.7063 | 1471.06 | 1103.295 | 2206.59 | 2666.2962 | 15997.7775 | CZ04 | A
CZ | CZ042 |  | CZ4213-789402-49099469-4/1U | COV Zelenky | 50.5914 | 13.7875 | 17700 | 17942 | NO | 112.1375 | 0 | 0 | 0 | 650.3975 | 3902.385 | CZ04 | C
CZ | CZ042 |  | CZ4214-703869-49099469-4/1U | COV Usti nad Labem - Nestemice | 50.6688 | 14.1077 | 169000 | 92709 | YES | 579.4312 | 1854.18 | 1390.635 | 2781.27 | 3360.7012 | 20164.2075 | CZ04 | A
CZ | CZ042 |  | CZ4214-778681-00267139-4/1U | COV Velke Brezno | 50.6652 | 14.1336 | 16050 | 15196 | NO | 94.975 | 0 | 0 | 0 | 550.855 | 3305.13 | CZ04 | A
CZ | CZ042 |  | CZ4215-776971-49099469-4/1U | COV Varnsdorf | 50.9056 | 14.6507 | 55450 | 20552 | YES | 128.45 | 411.04 | 308.28 | 616.56 | 745.01 | 4470.06 | CZ04 | A
CZ | CZ042 |  | CZ4216-794732-49099469-4/2U | COV Zatec | 50.331 | 13.5545 | 33333 | 23579 | YES | 147.3688 | 471.58 | 353.685 | 707.37 | 854.7387 | 5128.4325 | CZ04 | A
CZ | CZ051 |  | CZ5101-621382-49099469-4/1U | COV Ceska Lipa | 50.6787 | 14.5122 | 48150 | 26352 | YES | 164.7 | 527.04 | 395.28 | 790.56 | 955.26 | 5731.56 | CZ05 | A
CZ | CZ051 |  | CZ5101-628212-49099469-4/1U | COV Stare Splavy | 50.592 | 14.6271 | 8433 | 4473 | NO | 27.9563 | 0 | 0 | 0 | 162.1462 | 972.8775 | CZ05 | A
CZ | CZ051 |  | CZ5101-756466-49099469-4/1U | COV Straz pod Ralskem | 50.6964 | 14.7909 | 7000 | 3366 | NO | 21.0375 | 0 | 0 | 0 | 122.0175 | 732.105 | CZ05 | A
CZ | CZ051 |  | CZ5101-918423-49099469-4/3U | COV Mimon Hradcany - SIGMA | 50.6299 | 14.7398 | 9000 | 5721 | NO | 35.7563 | 0 | 0 | 0 | 207.3862 | 1244.3175 | CZ05 | A
CZ | CZ051 |  | CZ5102-635090-00262781-4/1U | COV Frydlant | 50.9212 | 15.0619 | 11000 | 4310 | NO | 26.9375 | 0 | 0 | 0 | 156.2375 | 937.425 | CZ05 | B
CZ | CZ051 |  | CZ5102-706523-25496565-4/1U | COV Nove Mesto pod Smrkem | 50.9306 | 15.2219 | 6400 | 1640 | NO | 10.25 | 0 | 0 | 0 | 59.45 | 356.7 | CZ05 | B
CZ | CZ010 |  | CZ1100-601527-00064581-4/2U | COV Ujezd nad Lesy | 50.0768 | 14.6549 | 14000 | 5602 | NO | 35.0125 | 0 | 0 | 0 | 203.0725 | 1218.435 | CZ01 | A
CZ | CZ010 |  | CZ1100-633330-00064581-4/1U | COV Uhrineves -Dubec | 50.0341 | 14.5938 | 14150 | 8133 | NO | 50.8313 | 0 | 0 | 0 | 294.8213 | 1768.9275 | CZ01 | A
CZ | CZ010 |  | CZ1100-643777-00064581-4/1U | COV Horni Pocernice-Certouzy | 50.0886 | 14.4252 | 10183 | 8446 | NO | 52.7875 | 0 | 0 | 0 | 306.1675 | 1837.005 | CZ01 | A
CZ | CZ010 |  | CZ1100-665444-00064581-4/1U | COV Klanovice | 50.0962 | 14.671 | 6055 | 2730 | NO | 17.0625 | 0 | 0 | 0 | 98.9625 | 593.775 | CZ01 | A
CZ | CZ010 |  | CZ1100-668591-00064581-4/1U | COV Kolovraty | 50.0137 | 14.6252 | 5400 | 2536 | NO | 15.85 | 0 | 0 | 0 | 91.93 | 551.58 | CZ01 | A
CZ | CZ010 |  | CZ1100-730106-00064581-4/1U | UCOV Praha | 50.0827 | 14.4691 | 1641600 | 1198805 | YES | 7492.5312 | 23976.1 | 17982.075 | 35964.15 | 43456.6813 | 260740.0875 | CZ01 | B
CZ | CZ010 |  | CZ1100-731552-00064581-4/1U | COV Miskovice | 50.1565 | 14.5415 | 15000 | 12866 | NO | 80.4125 | 0 | 0 | 0 | 466.3925 | 2798.355 | CZ01 | A
CZ | CZ010 |  | CZ1100-731641-00064581-4/1U | COV Kbely | 50.134 | 14.5469 | 7117 | 5413 | NO | 33.8313 | 0 | 0 | 0 | 196.2212 | 1177.3275 | CZ01 | A
CZ | CZ071 |  | CZ7109-667897-47674521-4/1U | COV Kojetin | 49.3487 | 17.3205 | 5833 | 11530 | NO | 72.0625 | 0 | 0 | 0 | 417.9625 | 2507.775 | CZ07 | C
CZ | CZ071 |  | CZ7110-699080-00296244-4/1U | COV Moravsky Beroun | 49.787 | 17.4425 | 5890 | 4761 | NO | 29.7562 | 0 | 0 | 0 | 172.5862 | 1035.5175 | CZ07 | B
CZ | CZ071 |  | CZ7110-763578-47150891-4/1U | COV Sternberk | 49.7179 | 17.2744 | 25600 | 16825 | NO | 105.1562 | 0 | 0 | 0 | 609.9062 | 3659.4375 | CZ07 | A
CZ | CZ071 |  | CZ7111-637203-64610276-4/1U | COV Hanusovice - pivovar a mesto | 50.0616 | 16.9257 | 31200 | 21434 | YES | 133.9625 | 428.68 | 321.51 | 643.02 | 776.9825 | 4661.895 | CZ07 | A
CZ | CZ071 |  | CZ7111-682837-00302899-4/1U | COV Libina | 49.8567 | 17.1073 | 18270 | 10396 | NO | 64.975 | 0 | 0 | 0 | 376.855 | 2261.13 | CZ07 | A
CZ | CZ071 |  | CZ7111-764264-47674954-4/1U | COV Sumperk | 49.9423 | 16.9594 | 50000 | 27259 | YES | 170.3688 | 545.18 | 408.885 | 817.77 | 988.1387 | 5928.8325 | CZ07 | C
CZ | CZ071 |  | CZ7111-779083-00303551-4/1U | COV Velke Losiny | 50.0125 | 17.036 | 6377 | 2714 | NO | 16.9625 | 0 | 0 | 0 | 98.3825 | 590.295 | CZ07 | A
CZ | CZ071 |  | CZ7112-774502-47675772-4/1U | COV Unicov | 49.7572 | 17.1249 | 20000 | 8284 | NO | 51.775 | 0 | 0 | 0 | 300.295 | 1801.77 | CZ07 | C
CZ | CZ071 |  | CZ7113-726176-00303232-4/1U | COV Postrelmov | 49.8966 | 16.9284 | 6300 | 4168 | NO | 26.05 | 0 | 0 | 0 | 151.09 | 906.54 | CZ07 | C
CZ | CZ071 |  | CZ7113-789429-47674954-4/1U | COV Zabreh | 49.8712 | 16.9021 | 57000 | 27486 | YES | 171.7875 | 549.72 | 412.29 | 824.58 | 996.3675 | 5978.205 | CZ07 | A
CZ | CZ072 |  | CZ7201-617121-49451871-4/1U | COV Bystrice pod Hostynem | 49.4006 | 17.6719 | 16817 | 7379 | NO | 46.1188 | 0 | 0 | 0 | 267.4888 | 1604.9325 | CZ07 | A
CZ | CZ072 |  | CZ7202-641057-49451871-4/1U | COV Holesov | 49.3273 | 17.5406 | 61867 | 17827 | YES | 111.4188 | 356.54 | 267.405 | 534.81 | 646.2287 | 3877.3725 | CZ07 | A
CZ | CZ072 |  | CZ7203-649309-49451871-4/1U | COV Hulin | 49.3043 | 17.478 | 7000 | 3769 | NO | 23.5563 | 0 | 0 | 0 | 136.6262 | 819.7575 | CZ07 | A
CZ | CZ072 |  | CZ7203-654230-49451871-4/1U | COV Chropyne | 49.3488 | 17.3744 | 6500 | 3898 | NO | 24.3625 | 0 | 0 | 0 | 141.3025 | 847.815 | CZ07 | C
CZ | CZ072 |  | CZ7203-674834-49451871-4/1U | COV Kromeriz | 49.2905 | 17.4242 | 66250 | 37425 | YES | 233.9062 | 748.5 | 561.375 | 1122.75 | 1356.6562 | 8139.9375 | CZ07 | A
CZ | CZ072 |  | CZ7204-688576-49454561-4/1U | COV Luhacovice | 49.0863 | 17.732 | 16170 | 9744 | NO | 60.9 | 0 | 0 | 0 | 353.22 | 2119.32 | CZ07 | A
CZ | CZ072 |  | CZ7204-750077-49454561-4/1U | COV Slavicin | 49.0799 | 17.8891 | 8045 | 7416 | NO | 46.35 | 0 | 0 | 0 | 268.83 | 1612.98 | CZ07 | A
CZ | CZ072 |  | CZ7205-701572-00284220-4/1U | COV Napajedla | 49.1608 | 17.5084 | 14400 | 3717 | NO | 23.2313 | 0 | 0 | 0 | 134.7413 | 808.4475 | CZ07 | B
CZ | CZ072 |  | CZ7205-716731-25342665-4/1U | COV Otrokovice | 49.2054 | 17.5144 | 168300 | 91489 | YES | 571.8062 | 1829.78 | 1372.335 | 2744.67 | 3316.4762 | 19898.8575 | CZ07 | A
CZ | CZ072 |  | CZ7206-733750-70238880-4/1U | COV Horni a Prostredni Becva | 49.443 | 18.2264 | 5000 | 1800 | NO | 11.25 | 0 | 0 | 0 | 65.25 | 391.5 | CZ07 | C
CZ | CZ072 |  | CZ7206-793787-70238880-4/1U | COV Zubri | 49.4603 | 18.0791 | 47000 | 25835 | NO | 161.4688 | 0 | 0 | 0 | 936.5187 | 5619.1125 | CZ07 | A
CZ | CZ010 |  | CZ1100-782378-00064581-4/1U | COV Vinor | 50.146 | 14.581 | 8923 | 3877 | NO | 24.2313 | 0 | 0 | 0 | 140.5413 | 843.2475 | CZ01 | A
CZ | CZ010 |  | CZ1100-791733-00064581-4/1U | COV Zbraslav | 49.9691 | 14.3866 | 13000 | 7026 | NO | 43.9125 | 0 | 0 | 0 | 254.6925 | 1528.155 | CZ01 | A
CZ | CZ020 |  | CZ2101-602191-00231401-4/1U | COV Benesov | 49.7867 | 14.6984 | 35330 | 30075 | YES | 187.9688 | 601.5 | 451.125 | 902.25 | 1090.2188 | 6541.3125 | CZ02 | A
CZ | CZ020 |  | CZ2101-746169-46356967-4/1U | COV Sazava | 49.875 | 14.8825 | 5060 | 2410 | NO | 15.0625 | 0 | 0 | 0 | 87.3625 | 524.175 | CZ02 | B
CZ | CZ051 |  | CZ5104-740900-00276057-4/1U | COV Rokytnice nad Jizerou | 50.7189 | 15.4221 | 6000 | 4468 | NO | 27.925 | 0 | 0 | 0 | 161.965 | 971.79 | CZ05 | A
CZ | CZ051 |  | CZ5104-781789-27061973-4/1U | COV Jilemnice - Devro | 50.6262 | 15.4962 | 28852 | 28953 | NO | 180.9562 | 0 | 0 | 0 | 1049.5462 | 6297.2775 | CZ05 | A
CZ | CZ020 |  | CZ2109-774499-00235075-4/1U | COV Unhost | 50.0816 | 14.1172 | 5000 | 4884 | NO | 30.525 | 0 | 0 | 0 | 177.045 | 1062.27 | CZ02 | B
CZ | CZ020 |  | CZ2110-668150-00235440-4/1U | COV Kolin | 50.0442 | 15.1864 | 34000 | 59130 | YES | 369.5625 | 1182.6 | 886.95 | 1773.9 | 2143.4625 | 12860.775 | CZ02 | C
CZ | CZ020 |  | CZ2110-718823-00239607-4/1U | COV Pecky | 50.0965 | 15.0406 | 7000 | 4280 | NO | 26.75 | 0 | 0 | 0 | 155.15 | 930.9 | CZ02 | A
CZ | CZ020 |  | CZ2111-779873-46356991-4/1U | COV Kralupy nad Vltavou | 50.2638 | 14.3103 | 59667 | 73194 | YES | 457.4625 | 1463.88 | 1097.91 | 2195.82 | 2653.2825 | 15919.695 | CZ02 | A
CZ | CZ020 |  | CZ2112-677710-46356967-4/1U | COV Kutna Hora | 49.9542 | 15.2901 | 36000 | 19597 | YES | 122.4813 | 391.94 | 293.955 | 587.91 | 710.3913 | 4262.3475 | CZ02 | A
CZ | CZ020 |  | CZ2112-793655-46356967-4/1U | COV Zruc I | 49.7477 | 15.089 | 5600 | 2288 | NO | 14.3 | 0 | 0 | 0 | 82.94 | 497.64 | CZ02 | A
CZ | CZ020 |  | CZ2113-602060-46357009-4/1U | COV Milovice -Benatska Vrutice | 50.2277 | 14.8526 | 8100 | 6502 | NO | 40.6375 | 0 | 0 | 0 | 235.6975 | 1414.185 | CZ02 | B
CZ | CZ020 |  | CZ2113-689556-00239402-4/1U | COV Lysa nad Labem - Litol | 50.184 | 14.8441 | 13950 | 6035 | NO | 37.7188 | 0 | 0 | 0 | 218.7687 | 1312.6125 | CZ02 | B
CZ | CZ020 |  | CZ2114-692816-46356991-4/1U | COV Melnik | 50.3277 | 14.4918 | 23900 | 16700 | NO | 104.375 | 0 | 0 | 0 | 605.375 | 3632.25 | CZ02 | C
CZ | CZ020 |  | CZ2115-601705-46356983-4/1U | COV Bela pod Bezdezem | 50.491 | 14.8402 | 5700 | 2851 | NO | 17.8188 | 0 | 0 | 0 | 103.3487 | 620.0925 | CZ02 | A
CZ | CZ063 |  | CZ6107-701564-60418885-4/1U | COV Namest nad Oslavou | 49.1971 | 16.1556 | 8000 | 4823 | NO | 30.1438 | 0 | 0 | 0 | 174.8337 | 1049.0025 | CZ06 | B
CZ | CZ063 |  | CZ6108-706418-43383513-4/1U | COV Nove Mesto na Morave | 49.5475 | 16.0726 | 18700 | 7673 | NO | 47.9563 | 0 | 0 | 0 | 278.1463 | 1668.8775 | CZ06 | B
CZ | CZ063 |  | CZ6109-717215-00248789-4/1U | COV Pacov | 49.4632 | 15.0234 | 7000 | 4221 | NO | 26.3812 | 0 | 0 | 0 | 153.0112 | 918.0675 | CZ06 | B
CZ | CZ063 |  | CZ6110-662577-00248380-4/1U | COV Kamenice nad Lipou | 49.2862 | 15.0778 | 7500 | 3746 | NO | 23.4125 | 0 | 0 | 0 | 135.7925 | 814.755 | CZ06 | B
CZ | CZ063 |  | CZ6110-718912-00248801-4/1U | COV Pelhrimov | 49.4418 | 15.2251 | 38167 | 24680 | YES | 154.25 | 493.6 | 370.2 | 740.4 | 894.65 | 5367.9 | CZ06 | B
CZ | CZ063 |  | CZ6110-723002-26048477-4/1U | COV Pocatky | 49.2554 | 15.2338 | 5000 | 1995 | NO | 12.4688 | 0 | 0 | 0 | 72.3187 | 433.9125 | CZ06 | A
CZ | CZ063 |  | CZ6110-797154-00249505-4/1U | COV Zirovnice | 49.2468 | 15.1769 | 8340 | 8298 | NO | 51.8625 | 0 | 0 | 0 | 300.8025 | 1804.815 | CZ06 | B
CZ | CZ063 |  | CZ6113-736562-60418885-4/1U | COV Trebic | 49.2148 | 15.9151 | 69833 | 52373 | YES | 327.3313 | 1047.46 | 785.595 | 1571.19 | 1898.5213 | 11391.1275 | CZ06 | C
CZ | CZ063 |  | CZ6114-778214-43383513-4/1U | COV Velka Bites | 49.2933 | 16.2333 | 9500 | 6052 | NO | 37.825 | 0 | 0 | 0 | 219.385 | 1316.31 | CZ06 | A
CZ | CZ063 |  | CZ6114-779091-43383513-4/1U | COV Velke Mezirici | 49.3418 | 16.0287 | 22300 | 12289 | NO | 76.8063 | 0 | 0 | 0 | 445.4763 | 2672.8575 | CZ06 | A
CZ | CZ063 |  | CZ6115-637106-43383513-4/1U | COV Zdar nad Sazavou | 49.5627 | 15.9193 | 34500 | 25347 | YES | 158.4188 | 506.94 | 380.205 | 760.41 | 918.8288 | 5512.9725 | CZ06 | A
CZ | CZ064 |  | CZ6201-600041-00279889-4/1U | COV Adamov | 49.2867 | 16.6673 | 7100 | 2441 | NO | 15.2563 | 0 | 0 | 0 | 88.4862 | 530.9175 | CZ06 | B
CZ | CZ064 |  | CZ6201-605018-49468952-4/1U | COV Blansko | 49.347 | 16.646 | 29376 | 13776 | YES | 86.1 | 275.52 | 206.64 | 413.28 | 499.38 | 2996.28 | CZ06 | B
CZ | CZ064 |  | CZ6202-608327-49468952-4/1U | COV A Boskovice | 49.4815 | 16.642 | 13060 | 10201 | NO | 63.7563 | 0 | 0 | 0 | 369.7862 | 2218.7175 | CZ06 | A
CZ | CZ064 |  | CZ6202-680711-00280518-4/1U | COV Letovice | 49.5322 | 16.5814 | 6380 | 1708 | NO | 10.675 | 0 | 0 | 0 | 61.915 | 371.49 | CZ06 | C
CZ | CZ064 |  | CZ6202-710415-00280755-4/1U | COV Olesnice | 49.55 | 16.422 | 5630 | 5274 | NO | 32.9625 | 0 | 0 | 0 | 191.1825 | 1147.095 | CZ06 | A
CZ | CZ064 |  | CZ6202-779237-00281247-4/1U | COV Velke Opatovice | 49.6125 | 16.6915 | 5266 | 2562 | NO | 16.0125 | 0 | 0 | 0 | 92.8725 | 557.235 | CZ06 | A
CZ | CZ064 |  | CZ6203-697931-46347275-4/1U | COV Brno - Modrice | 49.1284 | 16.6308 | 513000 | 499542 | YES | 3122.1375 | 9990.84 | 7493.13 | 14986.26 | 18108.3975 | 108650.385 | CZ06 | A
CZ | CZ064 |  | CZ6204-613584-49455168-4/1U | COV Breclav | 48.7466 | 16.8937 | 50543 | 27725 | YES | 173.2812 | 554.5 | 415.875 | 831.75 | 1005.0312 | 6030.1875 | CZ06 | A
CZ | CZ064 |  | CZ6204-679828-49455168-4/1U | COV Lednice | 48.7916 | 16.8223 | 12000 | 4256 | NO | 26.6 | 0 | 0 | 0 | 154.28 | 925.68 | CZ06 | C
CZ | CZ064 |  | CZ6206-640417-49454544-4/1U | COV Hodonin | 48.8414 | 17.1152 | 90000 | 46780 | YES | 292.375 | 935.6 | 701.7 | 1403.4 | 1695.775 | 10174.65 | CZ06 | A
CZ | CZ064 |  | CZ6206-734021-00285226-4/1U | COV Prusanky | 48.8338 | 16.9845 | 8605 | 3062 | NO | 19.1375 | 0 | 0 | 0 | 110.9975 | 665.985 | CZ06 | A
CZ | CZ064 |  | CZ6207-649864-49455168-4/1U | COV Hustopece | 48.9313 | 16.7495 | 9900 | 8361 | NO | 52.2563 | 0 | 0 | 0 | 303.0863 | 1818.5175 | CZ06 | A
CZ | CZ064 |  | CZ6207-779245-49455168-4/1U | COV Velke Pavlovice | 48.8938 | 16.8225 | 5400 | 8537 | NO | 53.3562 | 0 | 0 | 0 | 309.4662 | 1856.7975 | CZ06 | A
CZ | CZ064 |  | CZ6208-655741-49458892-4/1U | COV Ivancice | 49.0984 | 16.3927 | 13967 | 18035 | NO | 112.7188 | 0 | 0 | 0 | 653.7687 | 3922.6125 | CZ06 | A
CZ | CZ064 |  | CZ6209-781304-00282804-4/1U | COV Veverska Bityska | 49.2792 | 16.4514 | 6000 | 2957 | NO | 18.4812 | 0 | 0 | 0 | 107.1912 | 643.1475 | CZ06 | B
CZ | CZ064 |  | CZ6210-617270-49454544-4/1U | COV Bzenec | 48.9725 | 17.2993 | 22607 | 9964 | NO | 62.275 | 0 | 0 | 0 | 361.195 | 2167.17 | CZ06 | A
CZ | CZ064 |  | CZ6210-678431-00285030-4/1U | COV Kyjov | 48.9626 | 17.0895 | 26335 | 11585 | YES | 72.4062 | 231.7 | 173.775 | 347.55 | 419.9562 | 2519.7375 | CZ06 | B
CZ | CZ064 |  | CZ6210-695157-75833352-4/1U | COV Milotice | 48.9562 | 17.1268 | 7000 | 4566 | NO | 28.5375 | 0 | 0 | 0 | 165.5175 | 993.105 | CZ06 | B
CZ | CZ064 |  | CZ6210-760081-70863890-4/1U | COV Svatoborice-Mistrin | 48.9625 | 17.0896 | 8500 | 7189 | NO | 44.9312 | 0 | 0 | 0 | 260.6012 | 1563.6075 | CZ06 | B
CZ | CZ064 |  | CZ6211-694193-49455168-4/1U | COV Mikulov | 48.7965 | 16.6275 | 25000 | 10788 | YES | 67.425 | 215.76 | 161.82 | 323.64 | 391.065 | 2346.39 | CZ06 | A
CZ | CZ064 |  | CZ6212-695378-00293164-4/1U | COV Miroslav | 48.9355 | 16.342 | 21250 | 3562 | NO | 22.2625 | 0 | 0 | 0 | 129.1225 | 774.735 | CZ06 | C
CZ | CZ064 |  | CZ6212-699128-60418885-4/2U | COV Moravsky Krumlov - Zamecka | 49.0529 | 16.3074 | 5370 | 4016 | NO | 25.1 | 0 | 0 | 0 | 145.58 | 873.48 | CZ06 | B
CZ | CZ064 |  | CZ6213-724866-49455168-4/1U | COV Pohorelice | 48.9816 | 16.5324 | 6000 | 4901 | NO | 30.6312 | 0 | 0 | 0 | 177.6612 | 1065.9675 | CZ06 | A
CZ | CZ064 |  | CZ6214-766861-49458892-4/1U | COV Tetcice | 49.1701 | 16.4188 | 15000 | 12935 | NO | 80.8438 | 0 | 0 | 0 | 468.8937 | 2813.3625 | CZ06 | A
CZ | CZ064 |  | CZ6215-750301-49454587-4/1U | COV Slavkov u Brna | 49.1459 | 16.8629 | 9451 | 7696 | NO | 48.1 | 0 | 0 | 0 | 278.98 | 1673.88 | CZ06 | A
CZ | CZ064 |  | CZ6216-604551-70835004-4/1U | COV Bilovice nad Svitavou | 49.2418 | 16.6743 | 7750 | 4687 | NO | 29.2938 | 0 | 0 | 0 | 169.9038 | 1019.4225 | CZ06 | A
CZ | CZ064 |  | CZ6216-698504-00282120-4/1U | COV Moravany u Brna | 49.1429 | 16.5931 | 5500 | 7737 | NO | 48.3562 | 0 | 0 | 0 | 280.4662 | 1682.7975 | CZ06 | A
CZ | CZ064 |  | CZ6217-614114-49457004-4/1U | COV Brezina u Tisnova | 49.3211 | 16.4272 | 18000 | 13384 | NO | 83.65 | 0 | 0 | 0 | 485.17 | 2911.02 | CZ06 | B
CZ | CZ064 |  | CZ6218-756652-49454544-4/1U | COV Straznice | 48.8974 | 17.2946 | 9751 | 7852 | NO | 49.075 | 0 | 0 | 0 | 284.635 | 1707.81 | CZ06 | B
CZ | CZ064 |  | CZ6218-778583-00285447-4/1U | COV Velka nad Velickou | 48.8971 | 17.511 | 5500 | 1881 | NO | 11.7563 | 0 | 0 | 0 | 68.1863 | 409.1175 | CZ06 | A
CZ | CZ064 |  | CZ6218-780723-49454544-4/1U | COV Veseli nad Moravou | 48.9494 | 17.3681 | 16000 | 7184 | NO | 44.9 | 0 | 0 | 0 | 260.42 | 1562.52 | CZ06 | B
CZ | CZ064 |  | CZ6219-741922-49454587-4/1U | COV Rousinov | 49.1963 | 16.8802 | 5500 | 6805 | NO | 42.5312 | 0 | 0 | 0 | 246.6813 | 1480.0875 | CZ06 | A
CZ | CZ064 |  | CZ6219-788571-49454587-4/1U | COV Vyskov | 49.28 | 17.0187 | 38330 | 23736 | YES | 148.35 | 474.72 | 356.04 | 712.08 | 860.43 | 5162.58 | CZ06 | B
CZ | CZ064 |  | CZ6220-628123-45671745-4/1U | COV Znojmo | 48.8474 | 16.0926 | 99000 | 84612 | YES | 528.825 | 1692.24 | 1269.18 | 2538.36 | 3067.185 | 18403.11 | CZ06 | A
CZ | CZ064 |  | CZ6221-738921-00282456-4/1U | COV Rajhrad | 49.0831 | 16.6093 | 5000 | 4633 | NO | 28.9563 | 0 | 0 | 0 | 167.9462 | 1007.6775 | CZ06 | B
CZ | CZ064 |  | CZ6221-796701-49458841-4/1U | COV Zidlochovice | 49.0247 | 16.6234 | 6000 | 5134 | NO | 32.0875 | 0 | 0 | 0 | 186.1075 | 1116.645 | CZ06 | A
CZ | CZ071 |  | CZ7101-631949-47674521-4/1U | COV Hranice | 49.544 | 17.7183 | 30000 | 15767 | NOT KNOWN | 98.5438 | 0 | 0 | 0 | 571.5538 | 3429.3225 | CZ07 | B
CZ | CZ071 |  | CZ7102-621901-65138066-4/1U | COV Ceska Ves | 50.264 | 17.2429 | 41667 | 21598 | YES | 134.9875 | 431.96 | 323.97 | 647.94 | 782.9275 | 4697.565 | CZ07 | A
CZ | CZ071 |  | CZ7104-684261-47674521-4/1U | COV Lipnik nad Becvou | 49.5199 | 17.5882 | 13733 | 10201 | NO | 63.7563 | 0 | 0 | 0 | 369.7862 | 2218.7175 | CZ07 | A
CZ | CZ071 |  | CZ7105-685909-00299138-4/1U | COV Litovel | 49.7045 | 17.0946 | 40083 | 40639 | YES | 253.9938 | 812.78 | 609.585 | 1219.17 | 1473.1637 | 8838.9825 | CZ07 | B
CZ | CZ071 |  | CZ7106-698032-47674954-4/1U | COV Mohelnice | 49.7816 | 16.9379 | 21212 | 7689 | NO | 48.0563 | 0 | 0 | 0 | 278.7263 | 1672.3575 | CZ07 | A
CZ | CZ071 |  | CZ7107-640158-00299189-4/1U | COV Lutin | 49.5583 | 17.1527 | 6200 | 4012 | NO | 25.075 | 0 | 0 | 0 | 145.435 | 872.61 | CZ07 | B
CZ | CZ071 |  | CZ7107-710814-00299308-4/1U | COV Olomouc | 49.5675 | 17.2649 | 259500 | 172991 | YES | 1081.1938 | 3459.82 | 2594.865 | 5189.73 | 6270.9238 | 37625.5425 | CZ07 | A
CZ | CZ071 |  | CZ7108-672441-49451723-4/1U | COV Prostejov | 49.4643 | 17.1538 | 108000 | 58356 | YES | 364.725 | 1167.12 | 875.34 | 1750.68 | 2115.405 | 12692.43 | CZ07 | A
CZ | CZ071 |  | CZ7109-626708-47674521-4/1U | COV Prerov | 49.4502 | 17.3918 | 145000 | 90269 | YES | 564.1812 | 1805.38 | 1354.035 | 2708.07 | 3272.2512 | 19633.5075 | CZ07 | C
CZ | CZ072 |  | CZ7207-677345-49453866-4/1U | COV Uherske Hradiste | 49.0667 | 17.4395 | 99830 | 70891 | YES | 443.0687 | 1417.82 | 1063.365 | 2126.73 | 2569.7987 | 15418.7925 | CZ07 | B
CZ | CZ072 |  | CZ7207-773131-00291480-4/1U | COV Uhersky Ostroh | 48.9805 | 17.3819 | 7633 | 2947 | NO | 18.4187 | 0 | 0 | 0 | 106.8287 | 640.9725 | CZ07 | B
CZ | CZ072 |  | CZ7208-606979-49453866-4/1U | COV Bojkovice | 49.0422 | 17.8212 | 5800 | 3709 | NO | 23.1813 | 0 | 0 | 0 | 134.4513 | 806.7075 | CZ07 | A
CZ | CZ072 |  | CZ7208-772984-00291463-4/1U | COV Uhersky Brod | 49.0218 | 17.6306 | 74750 | 98665 | YES | 616.6562 | 1973.3 | 1479.975 | 2959.95 | 3576.6062 | 21459.6375 | CZ07 | A
CZ | CZ072 |  | CZ7209-613070-49454561-4/1U | COV Brumov - Bylnice | 49.0684 | 18.0043 | 16570 | 4119 | NO | 25.7438 | 0 | 0 | 0 | 149.3137 | 895.8825 | CZ07 | A
CZ | CZ072 |  | CZ7209-776319-49454561-4/1U | COV Valasske Klobouky | 49.119 | 18.0192 | 8000 | 1735 | NO | 10.8438 | 0 | 0 | 0 | 62.8937 | 377.3625 | CZ07 | C
CZ | CZ072 |  | CZ7210-776432-70238880-4/1U | COV Valasske Mezirici | 49.4871 | 17.9531 | 40000 | 58293 | YES | 364.3313 | 1165.86 | 874.395 | 1748.79 | 2113.1212 | 12678.7275 | CZ07 | A
CZ | CZ072 |  | CZ7210-791164-47674652-4/1U | COV Zasova | 49.4642 | 18.032 | 8434 | 3505 | NO | 21.9062 | 0 | 0 | 0 | 127.0562 | 762.3375 | CZ07 | A
CZ | CZ072 |  | CZ7211-750794-00284475-4/1U | COV Slusovice | 49.2383 | 17.7941 | 7600 | 3642 | NO | 22.7625 | 0 | 0 | 0 | 132.0225 | 792.135 | CZ07 | B
CZ | CZ072 |  | CZ7211-783196-49454561-4/1U | COV Vizovice | 49.2133 | 17.8264 | 8000 | 1479 | NO | 9.2438 | 0 | 0 | 0 | 53.6137 | 321.6825 | CZ07 | A
CZ | CZ072 |  | CZ7212-786764-47674652-4/1U | COV Vsetin | 49.3496 | 17.9696 | 41670 | 31154 | YES | 194.7125 | 623.08 | 467.31 | 934.62 | 1129.3325 | 6775.995 | CZ07 | A
CZ | CZ072 |  | CZ7213-635987-49454561-4/1U | COV Zlin | 49.2103 | 17.5806 | 207000 | 88954 | YES | 555.9625 | 1779.08 | 1334.31 | 2668.62 | 3224.5825 | 19347.495 | CZ07 | A
CZ | CZ080 |  | CZ8101-758396-45192588-4/1U | COV Studenka | 49.7056 | 18.0653 | 14000 | 4254 | NO | 26.5875 | 0 | 0 | 0 | 154.2075 | 925.245 | CZ08 | A
CZ | CZ080 |  | CZ8101-778664-45193665-4/1U | COV Bilovec-Velke Albrechtice | 49.7435 | 18.0766 | 5003 | 5545 | NO | 34.6562 | 0 | 0 | 0 | 201.0062 | 1206.0375 | CZ08 | C
CZ | CZ080 |  | CZ8102-707031-45193665-4/1U | COV Bohumin | 49.8961 | 18.3621 | 33680 | 12831 | NO | 80.1938 | 0 | 0 | 0 | 465.1237 | 2790.7425 | CZ08 | A
CZ | CZ080 |  | CZ8103-613169-00295892-4/1U | COV Bruntal | 49.9743 | 17.475 | 37383 | 19164 | YES | 119.775 | 383.28 | 287.46 | 574.92 | 694.695 | 4168.17 | CZ08 | A
CZ | CZ080 |  | CZ8115-707546-45193665-4/1U | COV Novy Jicin | 49.6137 | 18.0012 | 35000 | 26363 | YES | 164.7688 | 527.26 | 395.445 | 790.89 | 955.6588 | 5733.9525 | CZ08 | A
CZ | CZ080 |  | CZ8116-709085-45193665-4/1U | COV Odry | 49.6574 | 17.8414 | 6250 | 4324 | NO | 27.025 | 0 | 0 | 0 | 156.745 | 940.47 | CZ08 | A
CZ | CZ080 |  | CZ8117-711578-45193665-4/1U | COV Opava - Predmesti | 49.9311 | 17.928 | 149000 | 79268 | YES | 495.425 | 1585.36 | 1189.02 | 2378.04 | 2873.465 | 17240.79 | CZ08 | A
CZ | CZ080 |  | CZ8118-712493-45193665-4/1U | COV Orlova | 49.8665 | 18.4883 | 33330 | 22333 | NO | 139.5813 | 0 | 0 | 0 | 809.5713 | 4857.4275 | CZ08 | C
CZ | CZ080 |  | CZ8118-712493-45193665-4/2U | COV Petrvald | 49.8563 | 18.4178 | 5275 | 3939 | NO | 24.6188 | 0 | 0 | 0 | 142.7888 | 856.7325 | CZ08 | A
CZ | CZ080 |  | CZ8119-713767-00845451-4/1U | UCOV Ostrava - Privoz | 49.8555 | 18.2453 | 638850 | 235147 | YES | 1469.6688 | 4702.94 | 3527.205 | 7054.41 | 8524.0788 | 51144.4725 | CZ08 | A
CZ | CZ080 |  | CZ8119-714071-27804721-4/1U | UCOV CEZ Ostrava - Vitkovice | 49.8214 | 18.2838 | 10000 | 1616 | NO | 10.1 | 0 | 0 | 0 | 58.58 | 351.48 | CZ08 | A
CZ | CZ080 |  | CZ8119-714747-45193673-4/1U | COV Ostrava - Michalkovice | 49.8423 | 18.3523 | 5280 | 1987 | NO | 12.4188 | 0 | 0 | 0 | 72.0288 | 432.1725 | CZ08 | A
CZ | CZ080 |  | CZ8103-786080-25386344-4/1U | COV Vrbno pod Pradedem | 50.1127 | 17.3994 | 8500 | 2491 | NO | 15.5688 | 0 | 0 | 0 | 90.2988 | 541.7925 | CZ08 | A
CZ | CZ080 |  | CZ8104-652971-45193665-4/1U | COV Cesky Tesin - 04.1 | 49.7684 | 18.6093 | 30000 | 29548 | YES | 184.675 | 590.96 | 443.22 | 886.44 | 1071.115 | 6426.69 | CZ08 | A
CZ | CZ080 |  | CZ8105-634719-45193665-4/1U | COV Frenstat pod Radhostem | 49.5563 | 18.2012 | 20000 | 13210 | NO | 82.5625 | 0 | 0 | 0 | 478.8625 | 2873.175 | CZ08 | B
CZ | CZ080 |  | CZ8106-760676-45193665-4/1U | COV Frydek - Mistek | 49.7022 | 18.3225 | 164467 | 93622 | YES | 585.1375 | 1872.44 | 1404.33 | 2808.66 | 3393.7975 | 20362.785 | CZ08 | A
CZ | CZ080 |  | CZ8107-635171-45193665-4/1U | COV Frydlant nad Ostravici | 49.6041 | 18.3553 | 15000 | 5962 | NO | 37.2625 | 0 | 0 | 0 | 216.1225 | 1296.735 | CZ08 | B
CZ | CZ080 |  | CZ8109-639711-25914685-4/1U | COV Hlucin - Jasenky | 49.8851 | 18.1945 | 14609 | 5461 | NO | 34.1313 | 0 | 0 | 0 | 197.9613 | 1187.7675 | CZ08 | B
CZ | CZ052 |  | CZ5208-631426-25973495-4/1U | COV Vamberk | 50.1072 | 16.277 | 7500 | 1685 | NO | 10.5312 | 0 | 0 | 0 | 61.0812 | 366.4875 | CZ05 | B
CZ | CZ052 |  | CZ5208-670197-00274968-4/1U | COV Kostelec nad Orlici | 50.1224 | 16.1902 | 10000 | 4903 | NO | 30.6438 | 0 | 0 | 0 | 177.7337 | 1066.4025 | CZ05 | B
CZ | CZ052 |  | CZ5208-772429-75055384-4/1U | COV Tyniste nad Orlici | 50.1549 | 16.0648 | 10053 | 2840 | NO | 17.75 | 0 | 0 | 0 | 102.95 | 617.7 | CZ05 | A
CZ | CZ052 |  | CZ5209-621684-00272591-4/1U | COV Ceska Skalice - mestska | 50.3889 | 16.0219 | 10000 | 11507 | NO | 71.9188 | 0 | 0 | 0 | 417.1287 | 2502.7725 | CZ05 | B
CZ | CZ052 |  | CZ5209-701343-48172928-4/1U | COV Nachod | 50.3943 | 16.1573 | 45990 | 37784 | YES | 236.15 | 755.68 | 566.76 | 1133.52 | 1369.67 | 8218.02 | CZ05 | A
CZ | CZ052 |  | CZ5209-710369-00272566-4/1U | COV Cerveny Kostelec | 50.4705 | 16.0799 | 8000 | 2648 | NO | 16.55 | 0 | 0 | 0 | 95.99 | 575.94 | CZ05 | B
CZ | CZ052 |  | CZ5209-725323-00272949-4/1U | COV Police nad Metuji | 50.5257 | 16.2225 | 11950 | 4062 | NO | 25.3875 | 0 | 0 | 0 | 147.2475 | 883.485 | CZ05 | C
CZ | CZ052 |  | CZ5210-753823-00271888-4/1U | COV Nova a Stara Paka | 50.5189 | 15.4884 | 14000 | 12594 | NO | 78.7125 | 0 | 0 | 0 | 456.5325 | 2739.195 | CZ05 | A
CZ | CZ052 |  | CZ5211-706434-48172928-4/1U | COV Nove Mesto nad Metuji | 50.3454 | 16.1183 | 25000 | 8422 | NO | 52.6375 | 0 | 0 | 0 | 305.2975 | 1831.785 | CZ05 | B
CZ | CZ052 |  | CZ5212-707163-48172898-4/1U | COV Novy Bydzov | 50.2382 | 15.4982 | 9083 | 8671 | NO | 54.1938 | 0 | 0 | 0 | 314.3238 | 1885.9425 | CZ05 | A
CZ | CZ080 |  | CZ8110-656348-45193665-4/1U | COV Jablunkov | 49.5922 | 18.7462 | 8000 | 8870 | NO | 55.4375 | 0 | 0 | 0 | 321.5375 | 1929.225 | CZ08 | B
CZ | CZ052 |  | CZ5213-761800-00275336-4/1U | COV Rychnov nad Kneznou | 50.15 | 16.2619 | 24880 | 5943 | NO | 37.1438 | 0 | 0 | 0 | 215.4338 | 1292.6025 | CZ05 | C
CZ | CZ052 |  | CZ5214-606553-60108711-4/1U | COV Trutnov - Bohuslavice | 50.5533 | 15.9729 | 47500 | 29808 | YES | 186.3 | 596.16 | 447.12 | 894.24 | 1080.54 | 6483.24 | CZ05 | A
CZ | CZ052 |  | CZ5214-774651-00278386-4/1U | COV Upice | 50.4994 | 16.0266 | 7000 | 2460 | NO | 15.375 | 0 | 0 | 0 | 89.175 | 535.05 | CZ05 | A
CZ | CZ052 |  | CZ5215-645770-00277908-4/1U | COV Hostinne - Dlouha Louka | 50.5226 | 15.7397 | 8033 | 2268 | NO | 14.175 | 0 | 0 | 0 | 82.215 | 493.29 | CZ05 | B
CZ | CZ052 |  | CZ5215-762962-00278343-4/2U | COV Spindleruv Mlyn | 50.7238 | 15.5934 | 15000 | 6654 | NO | 41.5875 | 0 | 0 | 0 | 241.2075 | 1447.245 | CZ05 | A
CZ | CZ052 |  | CZ5215-786331-00278475-4/1U | COV Vrchlabi - Podhuri | 50.5926 | 15.6134 | 18800 | 11873 | NO | 74.2062 | 0 | 0 | 0 | 430.3962 | 2582.3775 | CZ05 | A
CZ | CZ053 |  | CZ5301-681377-60108118-4/1U | COV Ceska Trebova | 49.9849 | 16.3887 | 20000 | 26689 | NO | 166.8063 | 0 | 0 | 0 | 967.4762 | 5804.8575 | CZ05 | A
CZ | CZ053 |  | CZ5302-639303-48171590-4/1U | COV Hlinsko v Cechach | 49.7493 | 15.8902 | 61213 | 31912 | YES | 199.45 | 638.24 | 478.68 | 957.36 | 1156.81 | 6940.86 | CZ05 | A
CZ | CZ080 |  | CZ8111-664197-45193665-4/1U | COV Karvina | 49.8676 | 18.5226 | 88300 | 47131 | YES | 294.5688 | 942.62 | 706.965 | 1413.93 | 1708.4987 | 10250.9925 | CZ08 | A
CZ | CZ080 |  | CZ8112-669393-45193665-4/1U | COV Koprivnice | 49.612 | 18.1454 | 29000 | 22209 | NO | 138.8063 | 0 | 0 | 0 | 805.0763 | 4830.4575 | CZ08 | A
CZ | CZ080 |  | CZ8112-735370-45193665-4/1U | COV Pribor | 49.6479 | 18.1483 | 10860 | 6194 | NO | 38.7125 | 0 | 0 | 0 | 224.5325 | 1347.195 | CZ08 | B
CZ | CZ080 |  | CZ8113-674231-00300292-4/1U | COV Kravare | 49.9222 | 18.0405 | 7500 | 6533 | NO | 40.8313 | 0 | 0 | 0 | 236.8212 | 1420.9275 | CZ08 | B
CZ | CZ080 |  | CZ8114-674630-00296139-4/1U | COV Krnov | 50.081 | 17.7351 | 70000 | 121983 | YES | 762.3938 | 2439.66 | 1829.745 | 3659.49 | 4421.8837 | 26531.3025 | CZ08 | C
DE | DE733 | DEAG_HE066320200301 | DETP_HE066320200301 | Wildeck / Obersuhl | 50.9507 | 10.0449 | 5200 | 4300 | NOT KNOWN | 26.875 | 0 | 0 | 0 | 155.875 | 935.25 | DEG0 | A
DE | DE112 | DEAG_BW1155100000019 | DETP_BW1155100000019 | WEISSACH | 48.8479 | 8.9449 | 11500 | 11785 | NO | 73.6562 | 0 | 0 | 0 | 427.2062 | 2563.2375 | DE11 | B
DE | DE112 | DEAG_BW1155100000023 | DETP_BW1155100000023 | ZV AICHTAL - SCHÖNAICH | 48.6525 | 9.0871 | 25000 | 27167 | YES | 169.7938 | 543.34 | 407.505 | 815.01 | 984.8038 | 5908.8225 | DE11 | C
DE | DE112 | DEAG_BW1155100000026 | DETP_BW1155100000026 | WEIL IM SCHOENBUCH | 48.6273 | 9.0724 | 10000 | 7374 | NO | 46.0875 | 0 | 0 | 0 | 267.3075 | 1603.845 | DE11 | B
DE | DE112 | DEAG_BW1155100000027 | DETP_BW1155100000027 | WEIL DER STADT | 48.7611 | 8.8795 | 14500 | 7834 | NO | 48.9625 | 0 | 0 | 0 | 283.9825 | 1703.895 | DE11 | A
DE | DE112 | DEAG_BW1155100000029 | DETP_BW1155100000029 | SKA Waldenbuch | 48.6348 | 9.1622 | 14500 | 12779 | NO | 79.8688 | 0 | 0 | 0 | 463.2387 | 2779.4325 | DE11 | C
DE | DE112 | DEAG_BW1155100000031 | DETP_BW1155100000031 | STEINENBRONN | 48.6639 | 9.1095 | 9600 | 9389 | NO | 58.6813 | 0 | 0 | 0 | 340.3512 | 2042.1075 | DE11 | A
DE | DE112 | DEAG_BW1155100000033 | DETP_BW1155100000033 | AIDLINGEN | 48.6947 | 8.8995 | 11500 | 10851 | NO | 67.8188 | 0 | 0 | 0 | 393.3488 | 2360.0925 | DE11 | C
DE | DE112 | DEAG_BW1155100000034 | DETP_BW1155100000034 | ZV WÜRMURSPRUNG - HILDRIZHAUSEN | 48.6326 | 8.9775 | 13500 | 10209 | NO | 63.8063 | 0 | 0 | 0 | 370.0762 | 2220.4575 | DE11 | B
DE | DE112 | DEAG_BW1155100000066 | DETP_BW1155100000066 | ZV BÖBLINGEN-SINDELFINGEN II (DARMSHEIM) | 48.6982 | 8.9286 | 13800 | 12952 | NO | 80.95 | 0 | 0 | 0 | 469.51 | 2817.06 | DE11 | B
DE | DE112 | DEAG_BW1155100000067 | DETP_BW1155100000067 | ZV GÄRTRINGEN - NUFRINGEN | 48.6418 | 8.9298 | 36000 | 28688 | NO | 179.3 | 0 | 0 | 0 | 1039.94 | 6239.64 | DE11 | C
DE | DE111 | DEAG_BW1115100000001 | DETP_BW1115100000001 | Hauptklärwerk Mühlhausen | 48.8459 | 9.2407 | 1200000 | 821146 | YES | 5132.1625 | 16422.92 | 12317.19 | 24634.38 | 29766.5425 | 178599.255 | DE11 | A
DE | DE111 | DEAG_BW1115100000032 | DETP_BW1115100000032 | SKA BÜSNAU ( LFKW) / STUTTGART-BÜSNAU | 48.751 | 9.0897 | 9660 | 9976 | NO | 62.35 | 0 | 0 | 0 | 361.63 | 2169.78 | DE11 | B
DE | DE111 | DEAG_BW1115100000033 | DETP_BW1115100000033 | Klärwerk Möhringen / S - Möhringen | 48.7165 | 9.1691 | 160000 | 70849 | YES | 442.8063 | 1416.98 | 1062.735 | 2125.47 | 2568.2762 | 15409.6575 | DE11 | A
DE | DE112 | DEAG_BW1155100000016 | DETP_BW1155100000016 | BOEBLINGEN-SINDELFINGEN I | 48.6917 | 8.9827 | 250000 | 191692 | YES | 1198.075 | 3833.84 | 2875.38 | 5750.76 | 6948.835 | 41693.01 | DE11 | A
DE | DE112 | DEAG_BW1155100000017 | DETP_BW1155100000017 | ZV MITTLERES WÜRMTAL / WEIL DER STADT | 48.7971 | 8.8321 | 28000 | 14656 | NO | 91.6 | 0 | 0 | 0 | 531.28 | 3187.68 | DE12 | B
DE | DE112 | DEAG_BW1155100000018 | DETP_BW1155100000018 | ZV GRAFENAU-SCHAFHAUSEN | 48.7192 | 8.8987 | 10100 | 11075 | NO | 69.2188 | 0 | 0 | 0 | 401.4687 | 2408.8125 | DE11 | B
DE | DE113 | DEAG_BW1165100000015 | DETP_BW1165100000015 | LENNINGEN - GUTENBERG | 48.5346 | 9.4955 | 6500 | 3149 | NO | 19.6813 | 0 | 0 | 0 | 114.1513 | 684.9075 | DE11 | C
DE | DE113 | DEAG_BW1165100000020 | DETP_BW1165100000020 | LENNINGEN - OBERLENNINGEN | 48.5572 | 9.4629 | 8000 | 10878 | NO | 67.9875 | 0 | 0 | 0 | 394.3275 | 2365.965 | DE11 | A
DE | DE113 | DEAG_BW1165100000024 | DETP_BW1165100000024 | NECKARTAILFINGEN | 48.6139 | 9.2952 | 7000 | 7740 | NO | 48.375 | 0 | 0 | 0 | 280.575 | 1683.45 | DE11 | B
DE | DE113 | DEAG_BW1165100000025 | DETP_BW1165100000025 | NECKARTENZLINGEN | 48.5963 | 9.2443 | 17500 | 15453 | NO | 96.5813 | 0 | 0 | 0 | 560.1712 | 3361.0275 | DE11 | A
DE | DE113 | DEAG_BW1165100000028 | DETP_BW1165100000028 | NEUHAUSEN A.D.FILDERN | 48.6803 | 9.3005 | 15000 | 12621 | NO | 78.8813 | 0 | 0 | 0 | 457.5113 | 2745.0675 | DE11 | C
DE | DE113 | DEAG_BW1165100000030 | DETP_BW1165100000030 | NOTZINGEN | 48.6707 | 9.4405 | 8300 | 6073 | NO | 37.9563 | 0 | 0 | 0 | 220.1463 | 1320.8775 | DE11 | C
DE | DE113 | DEAG_BW1165100000032 | DETP_BW1165100000032 | NUERTINGEN | 48.6397 | 9.3374 | 75000 | 48268 | YES | 301.675 | 965.36 | 724.02 | 1448.04 | 1749.715 | 10498.29 | DE11 | A
DE | DE113 | DEAG_BW1165100000036 | DETP_BW1165100000036 | OSTFILDERN - NELLINGEN/ORT | 48.7027 | 9.2884 | 45000 | 33348 | YES | 208.425 | 666.96 | 500.22 | 1000.44 | 1208.865 | 7253.19 | DE11 | C
DE | DE113 | DEAG_BW1165100000038 | DETP_BW1165100000038 | OWEN | 48.5981 | 9.4447 | 16000 | 6278 | NO | 39.2375 | 0 | 0 | 0 | 227.5775 | 1365.465 | DE11 | B
DE | DE113 | DEAG_BW1165100000039 | DETP_BW1165100000039 | REICHENBACH A.D. FILS | 48.7042 | 9.4478 | 31000 | 10864 | NO | 67.9 | 0 | 0 | 0 | 393.82 | 2362.92 | DE11 | A
DE | DE113 | DEAG_BW1165100000040 | DETP_BW1165100000040 | WEILHEIM A.D. TECK | 48.627 | 9.5147 | 18000 | 12563 | NO | 78.5187 | 0 | 0 | 0 | 455.4087 | 2732.4525 | DE11 | A
DE | DE113 | DEAG_BW1165100000043 | DETP_BW1165100000043 | WERNAU (NECKAR) | 48.7026 | 9.4203 | 30000 | 8683 | NO | 54.2688 | 0 | 0 | 0 | 314.7588 | 1888.5525 | DE11 | A
DE | DE113 | DEAG_BW1165100000044 | DETP_BW1165100000044 | WOLFSCHLUGEN | 48.6448 | 9.2875 | 8300 | 5483 | NO | 34.2688 | 0 | 0 | 0 | 198.7588 | 1192.5525 | DE11 | B
DE | DE113 | DEAG_BW1165100000045 | DETP_BW1165100000045 | ZV UNTERES AICHTAL - AICHTAL-GRÖTZINGEN | 48.6319 | 9.2831 | 22000 | 12757 | NO | 79.7313 | 0 | 0 | 0 | 462.4412 | 2774.6475 | DE11 | C
DE | DE113 | DEAG_BW1165100000046 | DETP_BW1165100000046 | ZV PLOCHINGEN-ALTBACH-ZELL | 48.7253 | 9.3469 | 55000 | 30035 | YES | 187.7188 | 600.7 | 450.525 | 901.05 | 1088.7687 | 6532.6125 | DE11 | A
DE | DE113 | DEAG_BW1165100000047 | DETP_BW1165100000047 | ZV BEMPFLINGEN-RIEDERICH | 48.5787 | 9.2584 | 13000 | 13138 | NO | 82.1125 | 0 | 0 | 0 | 476.2525 | 2857.515 | DE11 | A
DE | DE113 | DEAG_BW1165100000048 | DETP_BW1165100000048 | ZV NEUFFENER TAL - FRICKENHAUSEN | 48.6004 | 9.3491 | 40000 | 13782 | NO | 86.1375 | 0 | 0 | 0 | 499.5975 | 2997.585 | DE11 | A
DE | DE113 | DEAG_BW1165100000049 | DETP_BW1165100000049 | ZV WENDLINGEN | 48.6843 | 9.3813 | 170213 | 96964 | YES | 606.025 | 1939.28 | 1454.46 | 2908.92 | 3514.945 | 21089.67 | DE11 | A
DE | DE113 | DEAG_BW1165100000094 | DETP_BW1165100000094 | STGT-PLIENINGEN | 48.7107 | 9.2307 | 133000 | 65822 | YES | 411.3875 | 1316.44 | 987.33 | 1974.66 | 2386.0475 | 14316.285 | DE11 | B
DE | DE114 | DEAG_BW1175100000052 | DETP_BW1175100000052 | Böhmenkirch - Treffelhausen | 48.6722 | 9.8969 | 8300 | 8931 | NO | 55.8188 | 0 | 0 | 0 | 323.7487 | 1942.4925 | DE11 | C
DE | DE114 | DEAG_BW1175100000053 | DETP_BW1175100000053 | Bad Boll | 48.6521 | 9.6229 | 8200 | 5186 | NO | 32.4125 | 0 | 0 | 0 | 187.9925 | 1127.955 | DE11 | C
DE | DE114 | DEAG_BW1175100000058 | DETP_BW1175100000058 | Ebersbach a. d. Fils | 48.7126 | 9.4991 | 23500 | 16378 | NO | 102.3625 | 0 | 0 | 0 | 593.7025 | 3562.215 | DE11 | C
DE | DE114 | DEAG_BW1175100000059 | DETP_BW1175100000059 | Geislingen a. d. Steige | 48.6329 | 9.8138 | 55000 | 53910 | YES | 336.9375 | 1078.2 | 808.65 | 1617.3 | 1954.2375 | 11725.425 | DE11 | A
DE | DE114 | DEAG_BW1175100000062 | DETP_BW1175100000062 | Göppingen | 48.704 | 9.6036 | 330000 | 257107 | YES | 1606.9188 | 5142.14 | 3856.605 | 7713.21 | 9320.1287 | 55920.7725 | DE11 | A
DE | DE114 | DEAG_BW1175100000070 | DETP_BW1175100000070 | Uhingen | 48.7159 | 9.5587 | 50000 | 22549 | YES | 140.9313 | 450.98 | 338.235 | 676.47 | 817.4012 | 4904.4075 | DE11 | A
DE | DE114 | DEAG_BW1175100000073 | DETP_BW1175100000073 | Schlierbach | 48.6744 | 9.5075 | 7000 | 5381 | NO | 33.6313 | 0 | 0 | 0 | 195.0613 | 1170.3675 | DE11 | B
DE | DE114 | DEAG_BW1175100000074 | DETP_BW1175100000074 | ZV Marbach - Krettenbachtal | 48.7449 | 9.6486 | 8000 | 4158 | NO | 25.9875 | 0 | 0 | 0 | 150.7275 | 904.365 | DE11 | B
DE | DE114 | DEAG_BW1175100000075 | DETP_BW1175100000075 | ZV AV Deggingen | 48.6082 | 9.7387 | 20000 | 12734 | NO | 79.5875 | 0 | 0 | 0 | 461.6075 | 2769.645 | DE11 | B
DE | DE114 | DEAG_BW1175100000078 | DETP_BW1175100000078 | ZV Mittlere Fils Salach | 48.6912 | 9.7257 | 85000 | 47307 | YES | 295.6687 | 946.14 | 709.605 | 1419.21 | 1714.8787 | 10289.2725 | DE11 | A
DE | DE115 | DEAG_BW1185100000004 | DETP_BW1185100000004 | SKA BESIGHEIM - BESIGHEIM | 49.004 | 9.1457 | 24000 | 11484 | NO | 71.775 | 0 | 0 | 0 | 416.295 | 2497.77 | DE11 | A
DE | DE115 | DEAG_BW1185100000005 | DETP_BW1185100000005 | SKA BIETIGHEIM - BIETIGHEIM-BISSINGEN | 48.9771 | 9.1493 | 140000 | 109690 | YES | 685.5625 | 2193.8 | 1645.35 | 3290.7 | 3976.2625 | 23857.575 | DE11 | C
DE | DE115 | DEAG_BW1185100000006 | DETP_BW1185100000006 | SKA BÖNNIGHEIM - BÖNNIGHEIM | 49.0383 | 9.1069 | 22000 | 12642 | NO | 79.0125 | 0 | 0 | 0 | 458.2725 | 2749.635 | DE11 | A
DE | DE115 | DEAG_BW1185100000007 | DETP_BW1185100000007 | SKA DITZINGEN - DITZINGEN | 48.8406 | 9.0564 | 120000 | 87437 | YES | 546.4813 | 1748.74 | 1311.555 | 2623.11 | 3169.5913 | 19017.5475 | DE11 | B
DE | DE115 | DEAG_BW1185100000008 | DETP_BW1185100000008 | SKA EGLOSHEIM - LUDWIGSBURG/EGLOSHEIM | 48.9141 | 9.1637 | 18400 | 11781 | NO | 73.6313 | 0 | 0 | 0 | 427.0612 | 2562.3675 | DE11 | A
DE | DE115 | DEAG_BW1185100000011 | DETP_BW1185100000011 | SKA ERLIGHEIM - ERLIGHEIM | 49.0141 | 9.1073 | 6000 | 4879 | NO | 30.4938 | 0 | 0 | 0 | 176.8638 | 1061.1825 | DE11 | B
DE | DE115 | DEAG_BW1185100000013 | DETP_BW1185100000013 | SKA FREIBERG - FREIBERG A.N. | 48.9412 | 9.1955 | 25000 | 13265 | NO | 82.9062 | 0 | 0 | 0 | 480.8562 | 2885.1375 | DE11 | A
DE | DE115 | DEAG_BW1185100000014 | DETP_BW1185100000014 | SKA GEMMRIGHEIM - GEMMRIGHEIM | 49.0359 | 9.1534 | 5500 | 6994 | NO | 43.7125 | 0 | 0 | 0 | 253.5325 | 1521.195 | DE11 | A
DE | DE115 | DEAG_BW1185100000015 | DETP_BW1185100000015 | SKA HÄLDENMÜHLE - MARBACH A.N. | 48.9505 | 9.252 | 80000 | 76716 | YES | 479.475 | 1534.32 | 1150.74 | 2301.48 | 2780.955 | 16685.73 | DE11 | B
DE | DE115 | DEAG_BW1185100000016 | DETP_BW1185100000016 | SKA HESSIGHEIM - HESSIGHEIM | 48.9864 | 9.1818 | 6500 | 6267 | NO | 39.1688 | 0 | 0 | 0 | 227.1787 | 1363.0725 | DE11 | B
DE | DE115 | DEAG_BW1185100000019 | DETP_BW1185100000019 | SKA KORNWESTHEIM - KORNWESTHEIM | 48.8636 | 9.213 | 41000 | 40727 | YES | 254.5438 | 814.54 | 610.905 | 1221.81 | 1476.3538 | 8858.1225 | DE11 | A
DE | DE115 | DEAG_BW1185100000020 | DETP_BW1185100000020 | SKA LEUDELSBACH - MARKGRÖNINGEN | 48.9139 | 9.0846 | 35000 | 27484 | YES | 171.775 | 549.68 | 412.26 | 824.52 | 996.295 | 5977.77 | DE11 | B
DE | DE115 | DEAG_BW1185100000021 | DETP_BW1185100000021 | SKA HOHENECK - LUDWIGSBURG/HOHENECK | 48.9202 | 9.2112 | 167000 | 86373 | YES | 539.8313 | 1727.46 | 1295.595 | 2591.19 | 3131.0212 | 18786.1275 | DE11 | B
DE | DE115 | DEAG_BW1185100000022 | DETP_BW1185100000022 | SKA POPPENWEILER - LUDWIGSBURG/POPPENWEILER | 48.9004 | 9.2603 | 31000 | 17682 | NO | 110.5125 | 0 | 0 | 0 | 640.9725 | 3845.835 | DE11 | A
DE | DE115 | DEAG_BW1185100000023 | DETP_BW1185100000023 | SKA MUNDELSHEIM - Mundelsheim | 49.0036 | 9.1998 | 8300 | 7932 | NO | 49.575 | 0 | 0 | 0 | 287.535 | 1725.21 | DE11 | A
DE | DE115 | DEAG_BW1185100000026 | DETP_BW1185100000026 | SKA OBERES BOTTWARTAL - OBERSTENFELD | 49.0134 | 9.3155 | 15000 | 9694 | NO | 60.5875 | 0 | 0 | 0 | 351.4075 | 2108.445 | DE11 | B
DE | DE115 | DEAG_BW1185100000035 | DETP_BW1185100000035 | SKA TALHAUSEN - MARKGRÖNINGEN | 48.9181 | 9.0667 | 75000 | 35819 | YES | 223.8688 | 716.38 | 537.285 | 1074.57 | 1298.4388 | 7790.6325 | DE11 | C
DE | DE115 | DEAG_BW1185100000036 | DETP_BW1185100000036 | SKA VAIHINGEN - VAIHINGEN A.D.ENZ | 48.9246 | 8.954 | 20000 | 14221 | NO | 88.8813 | 0 | 0 | 0 | 515.5113 | 3093.0675 | DE11 | A
DE | DE115 | DEAG_BW1185100000038 | DETP_BW1185100000038 | SKA WEIDACH - KIRCHHEIM A.N. | 49.0471 | 9.1494 | 6500 | 8017 | NO | 50.1062 | 0 | 0 | 0 | 290.6162 | 1743.6975 | DE11 | A
DE | DE115 | DEAG_BW1185100000173 | DETP_BW1185100000173 | SKA STRUDELBACH II - VAHINGEN A. D. ENZ/ENZWEIH. | 48.9202 | 8.9952 | 38000 | 30052 | YES | 187.825 | 601.04 | 450.78 | 901.56 | 1089.385 | 6536.31 | DE11 | A
DE | DE116 | DEAG_BW1195100000002 | DETP_BW1195100000002 | SKA SCHWAIKHEIM | 48.8747 | 9.3275 | 15000 | 13508 | NO | 84.425 | 0 | 0 | 0 | 489.665 | 2937.99 | DE11 | B
DE | DE116 | DEAG_BW1195100000003 | DETP_BW1195100000003 | SKA SULZBACH | 48.9961 | 9.4847 | 15000 | 9039 | NO | 56.4938 | 0 | 0 | 0 | 327.6638 | 1965.9825 | DE11 | C
DE | DE116 | DEAG_BW1195100000004 | DETP_BW1195100000004 | SKA WAIBLINGEN - HEGNACH | 48.8683 | 9.3054 | 25000 | 19609 | NO | 122.5562 | 0 | 0 | 0 | 710.8262 | 4264.9575 | DE11 | B
DE | DE116 | DEAG_BW1195100000005 | DETP_BW1195100000005 | SKA FELLBACH - ERBACH | 48.8142 | 9.3009 | 50000 | 34710 | YES | 216.9375 | 694.2 | 520.65 | 1041.3 | 1258.2375 | 7549.425 | DE11 | A
DE | DE116 | DEAG_BW1195100000006 | DETP_BW1195100000006 | SKA OPPENWEILER | 48.9797 | 9.4591 | 5800 | 4971 | NO | 31.0687 | 0 | 0 | 0 | 180.1987 | 1081.1925 | DE11 | A
DE | DE116 | DEAG_BW1195100000007 | DETP_BW1195100000007 | SKA WINNENDEN - ZIPFELBACHTAL | 48.8787 | 9.3776 | 28450 | 20592 | YES | 128.7 | 411.84 | 308.88 | 617.76 | 746.46 | 4478.76 | DE11 | B
DE | DE116 | DEAG_BW1195100000008 | DETP_BW1195100000008 | SKA ZV EICHBACHTAL | 48.9469 | 9.323 | 12000 | 11062 | NO | 69.1375 | 0 | 0 | 0 | 400.9975 | 2405.985 | DE11 | C
DE | DE116 | DEAG_BW1195100000011 | DETP_BW1195100000011 | SKA PLÜDERHAUSEN - URBACH | 48.8045 | 9.5688 | 40000 | 19821 | YES | 123.8813 | 396.42 | 297.315 | 594.63 | 718.5113 | 4311.0675 | DE11 | A
DE | DE116 | DEAG_BW1195100000013 | DETP_BW1195100000013 | SKA KERNEN - HALDENBACH | 48.7975 | 9.3533 | 12000 | 5066 | NO | 31.6625 | 0 | 0 | 0 | 183.6425 | 1101.855 | DE11 | B
DE | DE116 | DEAG_BW1195100000014 | DETP_BW1195100000014 | SKA KERNEN - BEIBACH | 48.8075 | 9.3387 | 6000 | 2888 | NO | 18.05 | 0 | 0 | 0 | 104.69 | 628.14 | DE11 | B
DE | DE116 | DEAG_BW1195100000015 | DETP_BW1195100000015 | SKA KERNEN - KRÄTTENBACH | 48.8158 | 9.3254 | 17000 | 6899 | NO | 43.1187 | 0 | 0 | 0 | 250.0887 | 1500.5325 | DE11 | A
DE | DE116 | DEAG_BW1195100000018 | DETP_BW1195100000018 | SKA MURRHARDT | 48.9865 | 9.5518 | 20000 | 22364 | NO | 139.775 | 0 | 0 | 0 | 810.695 | 4864.17 | DE11 | A
DE | DE116 | DEAG_BW1195100000024 | DETP_BW1195100000024 | SKA BERGLEN | 48.8508 | 9.4473 | 9100 | 10643 | NO | 66.5187 | 0 | 0 | 0 | 385.8087 | 2314.8525 | DE11 | B
DE | DE116 | DEAG_BW1195100000027 | DETP_BW1195100000027 | SKA WEINSTADT | 48.8152 | 9.3784 | 95000 | 43571 | YES | 272.3188 | 871.42 | 653.565 | 1307.13 | 1579.4488 | 9476.6925 | DE11 | A
DE | DE116 | DEAG_BW1195100000031 | DETP_BW1195100000031 | SKA ASPACH - KLÖPFERBACHTAL | 48.9547 | 9.3951 | 13000 | 11917 | NO | 74.4813 | 0 | 0 | 0 | 431.9913 | 2591.9475 | DE11 | C
DE | DE116 | DEAG_BW1195100000033 | DETP_BW1195100000033 | SKA ZV BUCHENBACHTAL | 48.9059 | 9.3651 | 45000 | 33828 | YES | 211.425 | 676.56 | 507.42 | 1014.84 | 1226.265 | 7357.59 | DE11 | B
DE | DE116 | DEAG_BW1195100000035 | DETP_BW1195100000035 | SKA ZV WEISSACHER TAL | 48.938 | 9.4676 | 25000 | 18093 | NO | 113.0813 | 0 | 0 | 0 | 655.8713 | 3935.2275 | DE11 | B
DE | DE116 | DEAG_BW1195100000036 | DETP_BW1195100000036 | SKA WELZHEIM | 48.8704 | 9.6443 | 15000 | 18817 | NO | 117.6063 | 0 | 0 | 0 | 682.1163 | 4092.6975 | DE11 | A
DE | DE116 | DEAG_BW1195100000038 | DETP_BW1195100000038 | SKA SCHORNDORF | 48.803 | 9.5011 | 56000 | 41870 | YES | 261.6875 | 837.4 | 628.05 | 1256.1 | 1517.7875 | 9106.725 | DE11 | B
DE | DE116 | DEAG_BW1195100000039 | DETP_BW1195100000039 | SKA WINTERBACH | 48.8029 | 9.4698 | 19000 | 8879 | NO | 55.4938 | 0 | 0 | 0 | 321.8637 | 1931.1825 | DE11 | A
DE | DE116 | DEAG_BW1195100000044 | DETP_BW1195100000044 | SKA RUDERSBERG - WIESLAUFTAL | 48.8531 | 9.5361 | 21000 | 11687 | NO | 73.0438 | 0 | 0 | 0 | 423.6538 | 2541.9225 | DE11 | B
DE | DE116 | DEAG_BW1195100000049 | DETP_BW1195100000049 | SKA BACKNANG - NEUSCHÖNTAL | 48.9357 | 9.3996 | 67000 | 26512 | YES | 165.7 | 530.24 | 397.68 | 795.36 | 961.06 | 5766.36 | DE11 | C
DE | DE116 | DEAG_BW1195100000050 | DETP_BW1195100000050 | SKA ALFDORF | 48.8417 | 9.7166 | 6000 | 4293 | NO | 26.8313 | 0 | 0 | 0 | 155.6213 | 933.7275 | DE11 | A
DE | DE116 | DEAG_BW1195100000054 | DETP_BW1195100000054 | SKA REMSHALDEN - GRUNBACH | 48.813 | 9.409 | 25000 | 12958 | NO | 80.9875 | 0 | 0 | 0 | 469.7275 | 2818.365 | DE11 | A
DE | DE116 | DEAG_BW1195100000056 | DETP_BW1195100000056 | SKA WAIBLINGEN | 48.8415 | 9.3109 | 70000 | 50178 | YES | 313.6125 | 1003.56 | 752.67 | 1505.34 | 1818.9525 | 10913.715 | DE11 | A
DE | DE117 | DEAG_BW1215100000017 | DETP_BW1215100000017 | SKA HEILBRONN | 49.182 | 9.2166 | 500000 | 249725 | YES | 1560.7812 | 4994.5 | 3745.875 | 7491.75 | 9052.5312 | 54315.1875 | DE11 | A
DE | DE118 | DEAG_BW1255100000002 | DETP_BW1255100000002 | SKA BAD RAPPENAU | 49.2589 | 9.1191 | 20000 | 34747 | NO | 217.1688 | 0 | 0 | 0 | 1259.5788 | 7557.4725 | DE11 | C
DE | DE118 | DEAG_BW1255100000003 | DETP_BW1255100000003 | SKA BAD RAPPENAU - BONFELD | 49.2096 | 9.1037 | 8000 | 7221 | NO | 45.1313 | 0 | 0 | 0 | 261.7613 | 1570.5675 | DE11 | B
DE | DE118 | DEAG_BW1255100000005 | DETP_BW1255100000005 | SKA BEILSTEIN | 49.0346 | 9.3169 | 9000 | 6854 | NO | 42.8375 | 0 | 0 | 0 | 248.4575 | 1490.745 | DE11 | A
DE | DE118 | DEAG_BW1255100000009 | DETP_BW1255100000009 | SKA EPPINGEN | 49.1414 | 8.9251 | 31350 | 26013 | YES | 162.5813 | 520.26 | 390.195 | 780.39 | 942.9712 | 5657.8275 | DE11 | A
DE | DE118 | DEAG_BW1255100000011 | DETP_BW1255100000011 | SKA GEMMINGEN | 49.1576 | 8.9694 | 9000 | 4807 | NO | 30.0438 | 0 | 0 | 0 | 174.2537 | 1045.5225 | DE11 | B
DE | DE118 | DEAG_BW1255100000013 | DETP_BW1255100000013 | SKA GUNDELSHEIM | 49.2878 | 9.1476 | 33300 | 8197 | YES | 51.2312 | 163.94 | 122.955 | 245.91 | 297.1412 | 1782.8475 | DE11 | B
DE | DE118 | DEAG_BW1255100000020 | DETP_BW1255100000020 | SKA LAUFFEN AM NECKAR | 49.0789 | 9.1674 | 41000 | 21181 | YES | 132.3812 | 423.62 | 317.715 | 635.43 | 767.8112 | 4606.8675 | DE11 | B
DE | DE118 | DEAG_BW1255100000022 | DETP_BW1255100000022 | SKA MÖCKMÜHL | 49.3062 | 9.3598 | 15000 | 9914 | NO | 61.9625 | 0 | 0 | 0 | 359.3825 | 2156.295 | DE11 | C
DE | DE118 | DEAG_BW1255100000026 | DETP_BW1255100000026 | SKA NEUDENAU - HERBOLZHEIM | 49.272 | 9.2512 | 7000 | 5161 | NO | 32.2563 | 0 | 0 | 0 | 187.0862 | 1122.5175 | DE11 | C
DE | DE118 | DEAG_BW1255100000029 | DETP_BW1255100000029 | SKA OEDHEIM | 49.2422 | 9.2404 | 9500 | 3941 | NO | 24.6312 | 0 | 0 | 0 | 142.8612 | 857.1675 | DE11 | B
DE | DE118 | DEAG_BW1255100000038 | DETP_BW1255100000038 | SKA ZV GKW SECKACHTAL | 49.3557 | 9.348 | 19000 | 11884 | NO | 74.275 | 0 | 0 | 0 | 430.795 | 2584.77 | DE11 | B
DE | DE118 | DEAG_BW1255100000039 | DETP_BW1255100000039 | SKA ZV GKA BRETTACHTAL | 49.2274 | 9.364 | 27300 | 14786 | NO | 92.4125 | 0 | 0 | 0 | 535.9925 | 3215.955 | DE11 | B
DE | DE118 | DEAG_BW1255100000040 | DETP_BW1255100000040 | SKA ZV GKA SULMTAL ELLHOFEN | 49.1538 | 9.3113 | 40000 | 37707 | YES | 235.6688 | 754.14 | 565.605 | 1131.21 | 1366.8787 | 8201.2725 | DE11 | B
DE | DE118 | DEAG_BW1255100000042 | DETP_BW1255100000042 | SKA AZV UNTERES KOCHERTAL | 49.257 | 9.2915 | 32000 | 26551 | YES | 165.9437 | 531.02 | 398.265 | 796.53 | 962.4737 | 5774.8425 | DE11 | B
DE | DE118 | DEAG_BW1255100000043 | DETP_BW1255100000043 | SKA ZV KW NECKARWESTHEIM | 49.0507 | 9.1769 | 9950 | 10203 | NO | 63.7688 | 0 | 0 | 0 | 369.8587 | 2219.1525 | DE11 | B
DE | DE118 | DEAG_BW1255100000044 | DETP_BW1255100000044 | SKA ZV UNTERES SULMTAL NECKARSULM | 49.2062 | 9.2182 | 200000 | 167048 | YES | 1044.05 | 3340.96 | 2505.72 | 5011.44 | 6055.49 | 36332.94 | DE11 | A
DE | DE118 | DEAG_BW1255100000045 | DETP_BW1255100000045 | SKA ZV GKA OBERE ZABER Güglingen Frauenzimmern | 49.0687 | 9.0471 | 20000 | 16579 | NO | 103.6187 | 0 | 0 | 0 | 600.9887 | 3605.9325 | DE11 | B
DE | DE118 | DEAG_BW1255100000046 | DETP_BW1255100000046 | SKA ZV GKA SCHOZACHTAL ILSFELD | 49.0532 | 9.226 | 35000 | 21756 | YES | 135.975 | 435.12 | 326.34 | 652.68 | 788.655 | 4731.93 | DE11 | C
DE | DE118 | DEAG_BW1255100000824 | DETP_BW1255100000824 | VKA AZV JAGST - KESSACH WIDDERN | 49.3198 | 9.4084 | 15925 | 15902 | NO | 99.3875 | 0 | 0 | 0 | 576.4475 | 3458.685 | DE11 | B
DE | DE119 | DEAG_BW1265100000005 | DETP_BW1265100000005 | SKA Forchtenberg | 49.2912 | 9.5515 | 5000 | 5743 | NO | 35.8938 | 0 | 0 | 0 | 208.1838 | 1249.1025 | DE11 | B
DE | DE119 | DEAG_BW1265100000010 | DETP_BW1265100000010 | SKA Ingelfingen-Criesbach | 49.3014 | 9.6332 | 6220 | 3454 | NO | 21.5875 | 0 | 0 | 0 | 125.2075 | 751.245 | DE11 | B
DE | DE119 | DEAG_BW1265100000014 | DETP_BW1265100000014 | SKA Krautheim | 49.3788 | 9.6303 | 11000 | 14368 | NO | 89.8 | 0 | 0 | 0 | 520.84 | 3125.04 | DE11 | A
DE | DE119 | DEAG_BW1265100000017 | DETP_BW1265100000017 | SKA Künzelsau | 49.2826 | 9.6811 | 19000 | 24065 | NO | 150.4062 | 0 | 0 | 0 | 872.3563 | 5234.1375 | DE11 | A
DE | DE119 | DEAG_BW1265100000021 | DETP_BW1265100000021 | SKA Kupferzell | 49.2309 | 9.6788 | 6800 | 4641 | NO | 29.0062 | 0 | 0 | 0 | 168.2362 | 1009.4175 | DE11 | B
DE | DE119 | DEAG_BW1265100000024 | DETP_BW1265100000024 | SKA Mulfingen | 49.3498 | 9.7876 | 5900 | 5697 | NO | 35.6063 | 0 | 0 | 0 | 206.5162 | 1239.0975 | DE11 | C
DE | DE119 | DEAG_BW1265100000026 | DETP_BW1265100000026 | SKA Neuenstein | 49.1985 | 9.5545 | 8335 | 8318 | NO | 51.9875 | 0 | 0 | 0 | 301.5275 | 1809.165 | DE11 | C
DE | DE119 | DEAG_BW1265100000030 | DETP_BW1265100000030 | SKA Niedernhall | 49.2904 | 9.6144 | 6000 | 5638 | NO | 35.2375 | 0 | 0 | 0 | 204.3775 | 1226.265 | DE11 | A
DE | DE119 | DEAG_BW1265100000031 | DETP_BW1265100000031 | SKA Öhringen | 49.2083 | 9.481 | 49500 | 34703 | NO | 216.8937 | 0 | 0 | 0 | 1257.9837 | 7547.9025 | DE11 | A
DE | DE119 | DEAG_BW1265100000035 | DETP_BW1265100000035 | SKA Schöntal | 49.3348 | 9.5137 | 6000 | 4485 | NO | 28.0312 | 0 | 0 | 0 | 162.5813 | 975.4875 | DE11 | C
DE | DE119 | DEAG_BW1265100000038 | DETP_BW1265100000038 | SKA Waldenburg | 49.2037 | 9.6469 | 9000 | 6183 | NO | 38.6438 | 0 | 0 | 0 | 224.1338 | 1344.8025 | DE11 | C
DE | DE119 | DEAG_BW1265100000040 | DETP_BW1265100000040 | SKA Weißbach | 49.293 | 9.5957 | 5500 | 2304 | NO | 14.4 | 0 | 0 | 0 | 83.52 | 501.12 | DE11 | B
DE | DE11A | DEAG_BW1275100000003 | DETP_BW1275100000003 | SKA Blaufelden-Blaufelden | 49.2874 | 9.9715 | 5000 | 6565 | NO | 41.0312 | 0 | 0 | 0 | 237.9812 | 1427.8875 | DE11 | B
DE | DE11A | DEAG_BW1275100000014 | DETP_BW1275100000014 | SKA Crailsheim-Crailsheim | 49.1532 | 10.0633 | 100000 | 114520 | YES | 715.75 | 2290.4 | 1717.8 | 3435.6 | 4151.35 | 24908.1 | DE11 | C
DE | DE11A | DEAG_BW1275100000021 | DETP_BW1275100000021 | SKA Fichtenau-Unterdeufstetten | 49.0462 | 10.2364 | 8000 | 6643 | NO | 41.5188 | 0 | 0 | 0 | 240.8088 | 1444.8525 | DE11 | B
DE | DE11A | DEAG_BW1275100000028 | DETP_BW1275100000028 | SKA Gaildorf | 49.0087 | 9.7619 | 18000 | 11729 | NO | 73.3063 | 0 | 0 | 0 | 425.1763 | 2551.0575 | DE11 | A
DE | DE11A | DEAG_BW1275100000034 | DETP_BW1275100000034 | SKA Ilshofen-Ilshofen | 49.1637 | 9.9163 | 8000 | 7565 | NO | 47.2812 | 0 | 0 | 0 | 274.2312 | 1645.3875 | DE11 | A
DE | DE11A | DEAG_BW1275100000040 | DETP_BW1275100000040 | SKA Kirchberg/Jagst-Kirchberg | 49.2064 | 9.9808 | 6400 | 5576 | NO | 34.85 | 0 | 0 | 0 | 202.13 | 1212.78 | DE11 | A
DE | DE11A | DEAG_BW1275100000051 | DETP_BW1275100000051 | SKA Mainhardt-Mainhardt | 49.0847 | 9.5515 | 7500 | 9411 | NO | 58.8188 | 0 | 0 | 0 | 341.1487 | 2046.8925 | DE11 | B
DE | DE11A | DEAG_BW1275100000061 | DETP_BW1275100000061 | SKA Rottal | 48.9962 | 9.687 | 10000 | 10198 | NO | 63.7375 | 0 | 0 | 0 | 369.6775 | 2218.065 | DE11 | C
DE | DE138 | DEAG_BW3355100000003 | DETP_BW3355100000003 | VKA Oberes Bibertal/Tengen | 47.7666 | 8.687 | 7500 | 5948 | NO | 37.175 | 0 | 0 | 0 | 215.615 | 1293.69 | DE13 | C
DE | DE138 | DEAG_BW3355100000004 | DETP_BW3355100000004 | SKA Radolfzell | 47.741 | 8.9818 | 67000 | 32962 | YES | 206.0125 | 659.24 | 494.43 | 988.86 | 1194.8725 | 7169.235 | DE13 | A
DE | DE11A | DEAG_BW1275100000062 | DETP_BW1275100000062 | SKA Obersontheim-Obersontheim | 49.0637 | 9.8962 | 7000 | 4771 | NO | 29.8187 | 0 | 0 | 0 | 172.9487 | 1037.6925 | DE11 | B
DE | DE11A | DEAG_BW1275100000064 | DETP_BW1275100000064 | SKA Rosengarten-Rieden | 49.0597 | 9.7113 | 9900 | 6718 | NO | 41.9875 | 0 | 0 | 0 | 243.5275 | 1461.165 | DE11 | B
DE | DE11A | DEAG_BW1275100000068 | DETP_BW1275100000068 | SKA Rot am See-Brettenfeld | 49.2567 | 10.0145 | 10000 | 5592 | NO | 34.95 | 0 | 0 | 0 | 202.71 | 1216.26 | DE11 | A
DE | DE11A | DEAG_BW1275100000073 | DETP_BW1275100000073 | SKA Satteldorf-Neidenfels | 49.1785 | 10.0596 | 9800 | 7845 | NO | 49.0312 | 0 | 0 | 0 | 284.3813 | 1706.2875 | DE11 | B
DE | DE11A | DEAG_BW1275100000074 | DETP_BW1275100000074 | SKA Schrozberg-Schrozberg | 49.3512 | 9.9866 | 19000 | 14917 | NO | 93.2313 | 0 | 0 | 0 | 540.7412 | 3244.4475 | DE11 | B
DE | DE11A | DEAG_BW1275100000079 | DETP_BW1275100000079 | SKA Schwäbisch Hall-Schwäbisch Hall | 49.1266 | 9.7332 | 85000 | 95009 | YES | 593.8062 | 1900.18 | 1425.135 | 2850.27 | 3444.0762 | 20664.4575 | DE11 | A
DE | DE11A | DEAG_BW1275100000080 | DETP_BW1275100000080 | SKA Schwäbisch Hall-Sulzdorf | 49.1022 | 9.8507 | 5800 | 6079 | NO | 37.9937 | 0 | 0 | 0 | 220.3637 | 1322.1825 | DE11 | B
DE | DE11A | DEAG_BW1275100000083 | DETP_BW1275100000083 | SKA Stimpfach-Stimpfach | 49.0639 | 10.0808 | 9950 | 5896 | NO | 36.85 | 0 | 0 | 0 | 213.73 | 1282.38 | DE11 | B
DE | DE11A | DEAG_BW1275100000089 | DETP_BW1275100000089 | SKA Vellberg-Vellberg | 49.0911 | 9.8786 | 7000 | 6398 | NO | 39.9875 | 0 | 0 | 0 | 231.9275 | 1391.565 | DE11 | B
DE | DE11B | DEAG_BW1285100000051 | DETP_BW1285100000051 | SKA BAD MERGENTHEIM | 49.5005 | 9.7498 | 50000 | 43210 | YES | 270.0625 | 864.2 | 648.15 | 1296.3 | 1566.3625 | 9398.175 | DE11 | A
DE | DE11B | DEAG_BW1285100000057 | DETP_BW1285100000057 | SKA UNTERSCHÜPF | 49.5158 | 9.6965 | 18300 | 14073 | NO | 87.9562 | 0 | 0 | 0 | 510.1462 | 3060.8775 | DE11 | B
DE | DE11B | DEAG_BW1285100000061 | DETP_BW1285100000061 | SKA CREGLINGEN | 49.4798 | 10.0191 | 5500 | 7487 | NO | 46.7937 | 0 | 0 | 0 | 271.4037 | 1628.4225 | DE11 | C
DE | DE11B | DEAG_BW1285100000066 | DETP_BW1285100000066 | SKA MONDFELD-BOXTAL | 49.7711 | 9.4008 | 6000 | 4068 | NO | 25.425 | 0 | 0 | 0 | 147.465 | 884.79 | DE11 | B
DE | DE11B | DEAG_BW1285100000071 | DETP_BW1285100000071 | SKA GRÜNSFELD | 49.6014 | 9.7369 | 11000 | 8192 | NO | 51.2 | 0 | 0 | 0 | 296.96 | 1781.76 | DE11 | B
DE | DE11B | DEAG_BW1285100000076 | DETP_BW1285100000076 | SKA KÜLSHEIM | 49.6785 | 9.5231 | 6500 | 4724 | NO | 29.525 | 0 | 0 | 0 | 171.245 | 1027.47 | DE11 | A
DE | DE11B | DEAG_BW1285100000079 | DETP_BW1285100000079 | SKA LAUDA-GERLACHSHEIM | 49.5807 | 9.707 | 34860 | 19954 | NO | 124.7125 | 0 | 0 | 0 | 723.3325 | 4339.995 | DE11 | B
DE | DE11B | DEAG_BW1285100000081 | DETP_BW1285100000081 | SKA VORBACHZIMMERN | 49.4291 | 9.9154 | 8900 | 6310 | NO | 39.4375 | 0 | 0 | 0 | 228.7375 | 1372.425 | DE11 | B
DE | DE11B | DEAG_BW1285100000083 | DETP_BW1285100000083 | SKA TAUBERBISCHOFSHEIM | 49.6343 | 9.6602 | 46700 | 23152 | YES | 144.7 | 463.04 | 347.28 | 694.56 | 839.26 | 5035.56 | DE11 | B
DE | DE11B | DEAG_BW1285100000085 | DETP_BW1285100000085 | SKA WEIKERSHEIM | 49.4724 | 9.8936 | 15000 | 7839 | NO | 48.9938 | 0 | 0 | 0 | 284.1638 | 1704.9825 | DE11 | B
DE | DE11B | DEAG_BW1285100000088 | DETP_BW1285100000088 | SKA WERTHEIM | 49.7841 | 9.4789 | 29000 | 19329 | NO | 120.8062 | 0 | 0 | 0 | 700.6762 | 4204.0575 | DE11 | A
DE | DE11B | DEAG_BW1285100000089 | DETP_BW1285100000089 | SKA WERTHEIM-OST | 49.7559 | 9.5674 | 7000 | 3349 | NO | 20.9313 | 0 | 0 | 0 | 121.4013 | 728.4075 | DE11 | C
DE | DE11B | DEAG_BW1285100000092 | DETP_BW1285100000092 | SKA WITTIGBACHTAL AZV | 49.606 | 9.8189 | 8500 | 2595 | NO | 16.2188 | 0 | 0 | 0 | 94.0687 | 564.4125 | DE11 | C
DE | DE11C | DEAG_BW1355100000050 | DETP_BW1355100000050 | SKA Giengen, Giengen | 48.6141 | 10.2533 | 35000 | 25480 | NO | 159.25 | 0 | 0 | 0 | 923.65 | 5541.9 | DE11 | A
DE | DE11C | DEAG_BW1355100000057 | DETP_BW1355100000057 | SKA Mergelstetten, Heidenheim | 48.6472 | 10.157 | 130000 | 84394 | YES | 527.4625 | 1687.88 | 1265.91 | 2531.82 | 3059.2825 | 18355.695 | DE11 | A
DE | DE11C | DEAG_BW1355100000058 | DETP_BW1355100000058 | SKA Schnaitheim, Heidenheim | 48.6961 | 10.1633 | 43500 | 13943 | YES | 87.1437 | 278.86 | 209.145 | 418.29 | 505.4337 | 3032.6025 | DE11 | A
DE | DE11C | DEAG_BW1355100000071 | DETP_BW1355100000071 | SKA Niederstotzingen, Niederstotzingen | 48.5328 | 10.2428 | 7800 | 5921 | NO | 37.0063 | 0 | 0 | 0 | 214.6363 | 1287.8175 | DE11 | A
DE | DE11C | DEAG_BW1355100000548 | DETP_BW1355100000548 | KA Itzelberg, Königsbronn (neu) | 48.7316 | 10.1458 | 13000 | 10782 | NO | 67.3875 | 0 | 0 | 0 | 390.8475 | 2345.085 | DE11 | B
DE | DE11D | DEAG_BW1365100000005 | DETP_BW1365100000005 | SKA Aalen, Aalen | 48.8538 | 10.0977 | 80000 | 51756 | YES | 323.475 | 1035.12 | 776.34 | 1552.68 | 1876.155 | 11256.93 | DE11 | A
DE | DE11D | DEAG_BW1365100000006 | DETP_BW1365100000006 | SKA Dewangen, Aalen | 48.8731 | 10.0177 | 5400 | 4374 | NO | 27.3375 | 0 | 0 | 0 | 158.5575 | 951.345 | DE11 | A
DE | DE11D | DEAG_BW1365100000008 | DETP_BW1365100000008 | SKA Unterkochen, Aalen | 48.8254 | 10.1185 | 33000 | 11883 | NO | 74.2687 | 0 | 0 | 0 | 430.7587 | 2584.5525 | DE11 | A
DE | DE11D | DEAG_BW1365100000013 | DETP_BW1365100000013 | SKA Schwäbisch Gmünd, Schwäbisch Gmünd | 48.7867 | 9.747 | 90000 | 77803 | YES | 486.2688 | 1556.06 | 1167.045 | 2334.09 | 2820.3587 | 16922.1525 | DE11 | C
DE | DE11D | DEAG_BW1365100000016 | DETP_BW1365100000016 | SKA Gschwend, Gschwend | 48.9225 | 9.7739 | 6600 | 2866 | NO | 17.9125 | 0 | 0 | 0 | 103.8925 | 623.355 | DE11 | C
DE | DE11D | DEAG_BW1365100000025 | DETP_BW1365100000025 | SKA Lorch-Waldhausen, Lorch | 48.7854 | 9.6279 | 18000 | 14531 | NO | 90.8188 | 0 | 0 | 0 | 526.7487 | 3160.4925 | DE11 | B
DE | DE11D | DEAG_BW1365100000026 | DETP_BW1365100000026 | SKA Mutlangen, Mutlangen | 48.8296 | 9.7709 | 6000 | 6347 | NO | 39.6688 | 0 | 0 | 0 | 230.0787 | 1380.4725 | DE11 | C
DE | DE11D | DEAG_BW1365100000028 | DETP_BW1365100000028 | SKA Oberkochen, Oberkochen | 48.7928 | 10.125 | 15000 | 15020 | NO | 93.875 | 0 | 0 | 0 | 544.475 | 3266.85 | DE11 | B
DE | DE11D | DEAG_BW1365100000033 | DETP_BW1365100000033 | SKA Waldstetten, Waldstetten | 48.7788 | 9.8132 | 7500 | 11501 | NO | 71.8813 | 0 | 0 | 0 | 416.9112 | 2501.4675 | DE11 | B
DE | DE11D | DEAG_BW1365100000035 | DETP_BW1365100000035 | SKA AZV Lauter-Rems, Böbingen | 48.8217 | 9.8954 | 41150 | 40836 | YES | 255.225 | 816.72 | 612.54 | 1225.08 | 1480.305 | 8881.83 | DE11 | C
DE | DE11D | DEAG_BW1365100000036 | DETP_BW1365100000036 | SKA AZV Niederalfingen, Aalen | 48.8932 | 10.0647 | 43000 | 48821 | YES | 305.1313 | 976.42 | 732.315 | 1464.63 | 1769.7613 | 10618.5675 | DE11 | C
DE | DE11D | DEAG_BW1365100000037 | DETP_BW1365100000037 | SKA AZV Leintal, Leinzell | 48.8465 | 9.918 | 10000 | 7682 | NO | 48.0125 | 0 | 0 | 0 | 278.4725 | 1670.835 | DE11 | C
DE | DE11D | DEAG_BW1365100000074 | DETP_BW1365100000074 | SKA Abtsgmünd, Abtsgmünd | 48.9017 | 9.9911 | 13000 | 8926 | NO | 55.7875 | 0 | 0 | 0 | 323.5675 | 1941.405 | DE11 | C
DE | DE11D | DEAG_BW1365100000081 | DETP_BW1365100000081 | SKA Bopfingen, Bopfingen | 48.8479 | 10.3794 | 28000 | 21201 | NO | 132.5062 | 0 | 0 | 0 | 768.5362 | 4611.2175 | DE11 | A
DE | DE11D | DEAG_BW1365100000088 | DETP_BW1365100000088 | SKA Schönau, Ellwangen | 48.9902 | 10.1171 | 32500 | 27966 | NO | 174.7875 | 0 | 0 | 0 | 1013.7675 | 6082.605 | DE11 | B
DE | DE11D | DEAG_BW1365100000091 | DETP_BW1365100000091 | SKA Haisterhofen, Ellwangen | 48.9203 | 10.1986 | 20000 | 16205 | NO | 101.2812 | 0 | 0 | 0 | 587.4312 | 3524.5875 | DE11 | C
DE | DE13A | DEAG_BW3375100000039 | DETP_BW3375100000039 | SKA Klettgau -OT Erzingen | 47.6308 | 8.3962 | 7000 | 8462 | NO | 52.8875 | 0 | 0 | 0 | 306.7475 | 1840.485 | DE13 | B
DE | DE13A | DEAG_BW3375100000040 | DETP_BW3375100000040 | SKA Küssaberg | 47.6129 | 8.2697 | 7500 | 6679 | NO | 41.7437 | 0 | 0 | 0 | 242.1137 | 1452.6825 | DE13 | B
DE | DE13A | DEAG_BW3375100000042 | DETP_BW3375100000042 | SKA Murg | 47.5546 | 8.0114 | 11000 | 11616 | NO | 72.6 | 0 | 0 | 0 | 421.08 | 2526.48 | DE13 | A
DE | DE13A | DEAG_BW3375100000043 | DETP_BW3375100000043 | SKA Rickenbach-Wickartsmühle | 47.6049 | 7.9882 | 5000 | 6483 | NO | 40.5188 | 0 | 0 | 0 | 235.0088 | 1410.0525 | DE13 | C
DE | DE13A | DEAG_BW3375100000049 | DETP_BW3375100000049 | SKA Stühlingen | 47.7316 | 8.4405 | 6300 | 4822 | NO | 30.1375 | 0 | 0 | 0 | 174.7975 | 1048.785 | DE13 | C
DE | DE13A | DEAG_BW3375100000052 | DETP_BW3375100000052 | SKA Todtmoos | 47.7276 | 7.9987 | 6000 | 3260 | NO | 20.375 | 0 | 0 | 0 | 118.175 | 709.05 | DE13 | C
DE | DE13A | DEAG_BW3375100000056 | DETP_BW3375100000056 | SKA Waldshut-Tiengen, Waldshut | 47.6157 | 8.1881 | 23000 | 13802 | NO | 86.2625 | 0 | 0 | 0 | 500.3225 | 3001.935 | DE13 | A
DE | DE13A | DEAG_BW3375100000058 | DETP_BW3375100000058 | SKA Wehr, AZV Wehr | 47.5823 | 7.9062 | 56400 | 24975 | YES | 156.0938 | 499.5 | 374.625 | 749.25 | 905.3438 | 5432.0625 | DE13 | A
DE | DE13A | DEAG_BW3375100000059 | DETP_BW3375100000059 | SKA Wutöschingen, AZV Mittleres Wutachtal | 47.6323 | 8.3441 | 9000 | 4660 | NO | 29.125 | 0 | 0 | 0 | 168.925 | 1013.55 | DE13 | C
DE | DE13A | DEAG_BW3375100000060 | DETP_BW3375100000060 | SKA Waldshut-Tiengen, AZV Klettgau-West | 47.622 | 8.2629 | 50000 | 56224 | YES | 351.4 | 1124.48 | 843.36 | 1686.72 | 2038.12 | 12228.72 | DE13 | B
DE | DE13A | DEAG_BW3375100000061 | DETP BW3375100000061 | SKA AZV VORDERES ALBTAL, ALBBRUCK | 47.5852 | 8.129 | 14500 | 9753 | NOT KNOWN | 60.9563 | 0 | 0 | 0 | 353.5462 | 2121.2775 | DE13 | B
DE | DE13A | DEAG_BW3375100000063 | DETP_BW3375100000063 | SKA Bad Säckingen | 47.5482 | 7.9343 | 47000 | 42839 | YES | 267.7438 | 856.78 | 642.585 | 1285.17 | 1552.9138 | 9317.4825 | DE13 | A
DE | DE13A | DEAG_BW3375100000064 | DETP_BW3375100000064 | SKA Laufenburg | 47.5546 | 8.0401 | 10000 | 10081 | NO | 63.0063 | 0 | 0 | 0 | 365.4362 | 2192.6175 | DE13 | A
DE | DE13A | DEAG_BW3375100000069 | DETP_BW3375100000069 | SKA Bernau | 47.7888 | 8.068 | 5000 | 3448 | NO | 21.55 | 0 | 0 | 0 | 124.99 | 749.94 | DE13 | A
DE | DE13A | DEAG_BW3375100000072 | DETP_BW3375100000072 | SKA St. Blasien (neue SKA) | 47.7496 | 8.1495 | 8000 | 4618 | NO | 28.8625 | 0 | 0 | 0 | 167.4025 | 1004.415 | DE13 | A
DE | DE141 | DEAG_BW4155100000025 | DETP_BW4155100000025 | SKA Mittelstadt | 48.5682 | 9.227 | 22500 | 10776 | NO | 67.35 | 0 | 0 | 0 | 390.63 | 2343.78 | DE11 | B
DE | DE141 | DEAG_BW4155100000026 | DETP_BW4155100000026 | SKA ENGSTINGEN-KOHLSTETTEN | 48.3999 | 9.3373 | 7200 | 6645 | NO | 41.5312 | 0 | 0 | 0 | 240.8812 | 1445.2875 | DE14 | B
DE | DE141 | DEAG_BW4155100000032 | DETP_BW4155100000032 | SKA MÜNSINGEN | 48.4086 | 9.454 | 22000 | 17252 | NO | 107.825 | 0 | 0 | 0 | 625.385 | 3752.31 | DE14 | C
DE | DE141 | DEAG_BW4155100000036 | DETP_BW4155100000036 | SKA PLIEZHAUSEN-RÜBGARTEN | 48.5606 | 9.1646 | 5000 | 3277 | NO | 20.4812 | 0 | 0 | 0 | 118.7912 | 712.7475 | DE14 | B
DE | DE141 | DEAG_BW4155100000037 | DETP_BW4155100000037 | SKA REUTLINGEN-NORD | 48.5525 | 9.2147 | 79000 | 24821 | YES | 155.1312 | 496.42 | 372.315 | 744.63 | 899.7613 | 5398.5675 | DE14 | A
DE | DE141 | DEAG_BW4155100000042 | DETP_BW4155100000042 | SKA RÖMERSTEIN-BÖHRINGEN | 48.4933 | 9.5048 | 7300 | 7025 | NO | 43.9062 | 0 | 0 | 0 | 254.6562 | 1527.9375 | DE14 | A
DE | DE141 | DEAG_BW4155100000046 | DETP_BW4155100000046 | AZV OBERES LAUCHERTTAL, MÄGERKINGEN | 48.2795 | 9.2152 | 24900 | 21715 | NO | 135.7188 | 0 | 0 | 0 | 787.1687 | 4723.0125 | DE14 | C
DE | DE141 | DEAG_BW4155100000048 | DETP_BW4155100000048 | SKA ZWIEFALTEN | 48.2198 | 9.4861 | 19500 | 10277 | NO | 64.2313 | 0 | 0 | 0 | 372.5412 | 2235.2475 | DE14 | C
DE | DE141 | DEAG_BW4155100000049 | DETP_BW4155100000049 | SKA ST. JOHANN-DEGENTAL | 48.4113 | 9.377 | 13670 | 9885 | NO | 61.7812 | 0 | 0 | 0 | 358.3312 | 2149.9875 | DE14 | C
DE | DE141 | DEAG_BW4155100000050 | DETP_BW4155100000050 | AZV Ermstal, Metzingen | 48.5532 | 9.2733 | 120000 | 86561 | YES | 541.0063 | 1731.22 | 1298.415 | 2596.83 | 3137.8362 | 18827.0175 | DE14 | A
DE | DE141 | DEAG_BW4155100000051 | DETP_BW4155100000051 | AZV OBERES ECHAZTAL, PFULLINGEN | 48.4806 | 9.2251 | 55555 | 71717 | YES | 448.2313 | 1434.34 | 1075.755 | 2151.51 | 2599.7413 | 15598.4475 | DE14 | A
DE | DE141 | DEAG_BW4155100000052 | DETP_BW4155100000052 | SKA REUTLINGEN-WEST | 48.5036 | 9.1652 | 140000 | 88165 | YES | 551.0312 | 1763.3 | 1322.475 | 2644.95 | 3195.9812 | 19175.8875 | DE14 | B
DE | DE142 | DEAG_BW4165100000054 | DETP_BW4165100000054 | SKA Bodelshausen | 48.4055 | 8.9602 | 8500 | 6551 | NO | 40.9438 | 0 | 0 | 0 | 237.4737 | 1424.8425 | DE14 | C
DE | DE142 | DEAG_BW4165100000055 | DETP_BW4165100000055 | AZV Schaichtal; Dettenhausen | 48.6063 | 9.1085 | 10000 | 5015 | NO | 31.3438 | 0 | 0 | 0 | 181.7937 | 1090.7625 | DE14 | A
DE | DE142 | DEAG_BW4165100000056 | DETP_BW4165100000056 | AZV Unteres Echaztal-Härten; Kirchentellinsfurt | 48.54 | 9.1534 | 31000 | 11837 | NO | 73.9813 | 0 | 0 | 0 | 429.0912 | 2574.5475 | DE14 | B
DE | DE142 | DEAG_BW4165100000057 | DETP_BW4165100000057 | SKA Rottenburg-Bad Niedernau | 48.4629 | 8.9026 | 12600 | 8294 | NO | 51.8375 | 0 | 0 | 0 | 300.6575 | 1803.945 | DE14 | C
DE | DE142 | DEAG_BW4165100000059 | DETP_BW4165100000059 | AZV Bondorf-Hailfingen; Hailfingen | 48.535 | 8.8753 | 9000 | 14574 | NO | 91.0875 | 0 | 0 | 0 | 528.3075 | 3169.845 | DE14 | B
DE | DE142 | DEAG_BW4165100000060 | DETP_BW4165100000060 | AZV Raum Ergenzingen; Ergenzingen | 48.4814 | 8.8191 | 13000 | 13477 | NO | 84.2313 | 0 | 0 | 0 | 488.5412 | 2931.2475 | DE14 | B
DE | DE142 | DEAG_BW4165100000063 | DETP_BW4165100000063 | AZV Börstingen; Börstingen | 48.4442 | 8.8118 | 7000 | 7885 | NO | 49.2812 | 0 | 0 | 0 | 285.8313 | 1714.9875 | DE14 | B
DE | DE142 | DEAG_BW4165100000064 | DETP_BW4165100000064 | AZV Steinlach-Wiesaz; Dußlingen | 48.4811 | 9.0647 | 115000 | 74484 | YES | 465.525 | 1489.68 | 1117.26 | 2234.52 | 2700.045 | 16200.27 | DE14 | C
DE | DE142 | DEAG_BW4165100000065 | DETP_BW4165100000065 | SKA Rottenburg-Kiebingen | 48.4841 | 8.9784 | 45800 | 39282 | YES | 245.5125 | 785.64 | 589.23 | 1178.46 | 1423.9725 | 8543.835 | DE14 | C
DE | DE142 | DEAG_BW4165100000066 | DETP_BW4165100000066 | SKA Tübingen | 48.5299 | 9.0973 | 137500 | 105108 | YES | 656.925 | 2102.16 | 1576.62 | 3153.24 | 3810.165 | 22860.99 | DE14 | A
DE | DE143 | DEAG_BW4175100000002 | DETP_BW4175100000002 | SKA Mühringen (Horb) des AZV Unteres Eyachtal | 48.4268 | 8.7643 | 10000 | 8285 | NO | 51.7812 | 0 | 0 | 0 | 300.3312 | 1801.9875 | DE12 | B
DE | DE143 | DEAG_BW4175100000003 | DETP_BW4175100000003 | SKA Bisingen | 48.3134 | 8.8822 | 18700 | 16078 | NO | 100.4875 | 0 | 0 | 0 | 582.8275 | 3496.965 | DE14 | B
DE | DE143 | DEAG_BW4175100000004 | DETP_BW4175100000004 | SKA Burladingen | 48.2874 | 9.1459 | 24800 | 16782 | NO | 104.8875 | 0 | 0 | 0 | 608.3475 | 3650.085 | DE14 | C
DE | DE11D | DEAG_BW1365100000100 | DETP_BW1365100000100 | SKA Lauchheim, Lauchheim | 48.8733 | 10.2363 | 6000 | 5467 | NO | 34.1688 | 0 | 0 | 0 | 198.1788 | 1189.0725 | DE11 | A
DE | DE11D | DEAG_BW1365100000117 | DETP_BW1365100000117 | SKA Schwabsberg, Rainau | 48.9336 | 10.1371 | 9250 | 4632 | NO | 28.95 | 0 | 0 | 0 | 167.91 | 1007.46 | DE11 | B
DE | DE11D | DEAG_BW1365100000133 | DETP_BW1365100000133 | SKA Westhausen, Westhausen | 48.8943 | 10.1836 | 6700 | 7976 | NO | 49.85 | 0 | 0 | 0 | 289.13 | 1734.78 | DE11 | B
DE | DE122 | DEAG_BW2125100000014 | DETP_BW2125100000014 | SKA Karlsruhe Neureut | 49.0445 | 8.3594 | 875000 | 519247 | YES | 3245.2938 | 10384.94 | 7788.705 | 15577.41 | 18822.7038 | 112936.2225 | DE12 | A
DE | DE123 | DEAG_BW2155100000015 | DETP_BW2155100000015 | EGGENSTEIN-LEOPOLDSHAFEN KLA Leopoldshafen | 49.1065 | 8.398 | 20000 | 21379 | NO | 133.6188 | 0 | 0 | 0 | 774.9887 | 4649.9325 | DE12 | B
DE | DE123 | DEAG_BW2155100000016 | DETP_BW2155100000016 | KRAICHTAL KLA Kraichtal | 49.1522 | 8.6512 | 21000 | 25390 | NO | 158.6875 | 0 | 0 | 0 | 920.3875 | 5522.325 | DE12 | C
DE | DE123 | DEAG_BW2155100000017 | DETP_BW2155100000017 | LINKENHEIM-HOCHSTETTEN KLA Linkenheim-Hochstetten | 49.1446 | 8.4019 | 16000 | 14880 | NO | 93 | 0 | 0 | 0 | 539.4 | 3236.4 | DE12 | B
DE | DE123 | DEAG_BW2155100000018 | DETP_BW2155100000018 | ÖSTRINGEN KLA Östringen | 49.2153 | 8.6889 | 12500 | 10307 | NO | 64.4188 | 0 | 0 | 0 | 373.6288 | 2241.7725 | DE12 | B
DE | DE123 | DEAG_BW2155100000019 | DETP_BW2155100000019 | Östringen KLA Odenheim | 49.1827 | 8.7239 | 8000 | 10226 | NO | 63.9125 | 0 | 0 | 0 | 370.6925 | 2224.155 | DE12 | C
DE | DE123 | DEAG_BW2155100000020 | DETP_BW2155100000020 | PFINZTAL KLA Berghausen | 49.0082 | 8.5179 | 19000 | 23246 | NO | 145.2875 | 0 | 0 | 0 | 842.6675 | 5056.005 | DE12 | A
DE | DE123 | DEAG_BW2155100000021 | DETP_BW2155100000021 | PHILIPPSBURG KLA Philippsburg | 49.2446 | 8.4589 | 23500 | 14808 | NO | 92.55 | 0 | 0 | 0 | 536.79 | 3220.74 | DE12 | A
DE | DE123 | DEAG_BW2155100000024 | DETP_BW2155100000024 | RHEINSTETTEN KLA Mörsch | 48.9743 | 8.2856 | 14000 | 17081 | NO | 106.7563 | 0 | 0 | 0 | 619.1862 | 3715.1175 | DE12 | C
DE | DE123 | DEAG_BW2155100000025 | DETP_BW2155100000025 | STUTENSEE KLA Blankenloch | 49.0716 | 8.4802 | 15000 | 11288 | NO | 70.55 | 0 | 0 | 0 | 409.19 | 2455.14 | DE12 | B
DE | DE123 | DEAG_BW2155100000027 | DETP_BW2155100000027 | UBSTADT-WEIHER KLA Ubstadt-Weiher | 49.1838 | 8.6316 | 18000 | 18123 | NO | 113.2688 | 0 | 0 | 0 | 656.9588 | 3941.7525 | DE12 | B
DE | DE123 | DEAG_BW2155100000028 | DETP_BW2155100000028 | AV ALBTAL KLA Ettlingen-Neurod | 48.9187 | 8.4539 | 40000 | 66535 | NO | 415.8438 | 0 | 0 | 0 | 2411.8937 | 14471.3625 | DE12 | C
DE | DE123 | DEAG_BW2155100000029 | DETP_BW2155100000029 | AV AM WALZBACH KLA Weingarten | 49.0714 | 8.5147 | 29200 | 19134 | NO | 119.5875 | 0 | 0 | 0 | 693.6075 | 4161.645 | DE12 | B
DE | DE123 | DEAG_BW2155100000030 | DETP_BW2155100000030 | AV KAMMERFORST KLA Karlsdorf-Neuthard | 49.1372 | 8.5239 | 28500 | 25597 | NO | 159.9813 | 0 | 0 | 0 | 927.8913 | 5567.3475 | DE12 | A
DE | DE123 | DEAG_BW2155100000031 | DETP_BW2155100000031 | AV KRAICHBACHNIEDERUNG KLA Kronau | 49.2305 | 8.6398 | 33000 | 30158 | NO | 188.4875 | 0 | 0 | 0 | 1093.2275 | 6559.365 | DE12 | A
DE | DE123 | DEAG_BW2155100000032 | DETP_BW2155100000032 | AV OBERER KRAICHBACH KLA Flehingen | 49.0939 | 8.7591 | 35000 | 26635 | NO | 166.4688 | 0 | 0 | 0 | 965.5187 | 5793.1125 | DE12 | C
DE | DE123 | DEAG_BW2155100000033 | DETP_BW2155100000033 | AV PFINZ-U. RENNACHTAL KLA Ittersbach | 48.8717 | 8.5204 | 18000 | 13862 | NO | 86.6375 | 0 | 0 | 0 | 502.4975 | 3014.985 | DE12 | B
DE | DE123 | DEAG_BW2155100000034 | DETP_BW2155100000034 | AV WAGBACH KLA Waghäusel | 49.2582 | 8.5247 | 40200 | 32445 | YES | 202.7812 | 648.9 | 486.675 | 973.35 | 1176.1312 | 7056.7875 | DE12 | C
DE | DE123 | DEAG_BW2155100000035 | DETP_BW2155100000035 | AV WEIßACH-U. OB.SAALBACHTAL KLA Heidelsheim | 49.1129 | 8.6367 | 100000 | 107483 | YES | 671.7688 | 2149.66 | 1612.245 | 3224.49 | 3896.2587 | 23377.5525 | DE12 | C
DE | DE123 | DEAG_BW2155100000036 | DETP_BW2155100000036 | VG GRABEN-NEUDORF KLA Dettenheim | 49.1721 | 8.4037 | 30000 | 21157 | NO | 132.2313 | 0 | 0 | 0 | 766.9412 | 4601.6475 | DE12 | C
DE | DE123 | DEAG_BW2155100000037 | DETP_BW2155100000037 | BRUCHSAL KLA Bruchsal | 49.1417 | 8.5949 | 75000 | 73929 | YES | 462.0563 | 1478.58 | 1108.935 | 2217.87 | 2679.9262 | 16079.5575 | DE12 | A
DE | DE123 | DEAG_BW2155100000038 | DETP_BW2155100000038 | AV BRUCHNIEDERUNG KLA Oberhausen-Rheinhausen | 49.2827 | 8.5029 | 26300 | 21856 | NO | 136.6 | 0 | 0 | 0 | 792.28 | 4753.68 | DE12 | C
DE | DE124 | DEAG_BW2165100000001 | DETP_BW2165100000001 | KLA HÜGELSHEIM | 48.8052 | 8.1119 | 10000 | 4945 | NO | 30.9062 | 0 | 0 | 0 | 179.2562 | 1075.5375 | DE12 | B
DE | DE124 | DEAG_BW2165100000004 | DETP_BW2165100000004 | KLA RHEINMÜNSTER-SÖLLINGEN | 48.7842 | 8.0585 | 13300 | 5178 | NO | 32.3625 | 0 | 0 | 0 | 187.7025 | 1126.215 | DE12 | B
DE | DE124 | DEAG_BW2165100000006 | DETP_BW2165100000006 | GKA BADEN-BADEN-SINZHEIM | 48.7838 | 8.1608 | 200000 | 137766 | YES | 861.0375 | 2755.32 | 2066.49 | 4132.98 | 4994.0175 | 29964.105 | DE12 | C
DE | DE124 | DEAG_BW2165100000007 | DETP_BW2165100000007 | AV BÜHL-U. UMGEBUNG KLA VIMBUCH | 48.723 | 8.1235 | 167000 | 65570 | YES | 409.8125 | 1311.4 | 983.55 | 1967.1 | 2376.9125 | 14261.475 | DE12 | A
DE | DE124 | DEAG_BW2165100000009 | DETP_BW2165100000009 | GVV DURMERSHEIM KLA AU AM RHEIN | 48.9614 | 8.2535 | 30000 | 39530 | NO | 247.0625 | 0 | 0 | 0 | 1432.9625 | 8597.775 | DE12 | C
DE | DE124 | DEAG_BW2165100000010 | DETP_BW2165100000010 | KLA GERNSBACH AV MITTLERES MURGTAL | 48.7763 | 8.3382 | 25000 | 25448 | NO | 159.05 | 0 | 0 | 0 | 922.49 | 5534.94 | DE12 | B
DE | DE124 | DEAG_BW2165100000011 | DETP_BW2165100000011 | KLA GAGGENAU-ROTENFELS AV MURG | 48.8247 | 8.2912 | 60000 | 41444 | YES | 259.025 | 828.88 | 621.66 | 1243.32 | 1502.345 | 9014.07 | DE12 | A
DE | DE112 | DEAG_BW1155100000069 | DETP_BW1155100000069 | ZV GÄU-AMMER - HERRENBERG | 48.5657 | 8.8987 | 80000 | 63953 | YES | 399.7063 | 1279.06 | 959.295 | 1918.59 | 2318.2962 | 13909.7775 | DE11 | B
DE | DE112 | DEAG_BW1155100000080 | DETP_BW1155100000080 | EHNINGEN | 48.6634 | 8.9182 | 17100 | 11038 | NO | 68.9875 | 0 | 0 | 0 | 400.1275 | 2400.765 | DE11 | C
DE | DE112 | DEAG_BW1155100000081 | DETP_BW1155100000081 | LEONBERG - MITTLERES GLEMSTAL | 48.8146 | 9.0424 | 90000 | 77225 | YES | 482.6562 | 1544.5 | 1158.375 | 2316.75 | 2799.4062 | 16796.4375 | DE11 | C
DE | DE112 | DEAG_BW1155100000085 | DETP_BW1155100000085 | MAGSTADT | 48.7505 | 8.9487 | 18000 | 13212 | NO | 82.575 | 0 | 0 | 0 | 478.935 | 2873.61 | DE11 | B
DE | DE112 | DEAG_BW1155100000087 | DETP_BW1155100000087 | RENNINGEN | 48.7701 | 8.9216 | 25400 | 16699 | NO | 104.3687 | 0 | 0 | 0 | 605.3387 | 3632.0325 | DE11 | A
DE | DE112 | DEAG_BW1155100000088 | DETP_BW1155100000088 | RUTESHEIM | 48.801 | 8.9457 | 11700 | 11008 | NO | 68.8 | 0 | 0 | 0 | 399.04 | 2394.24 | DE11 | A
DE | DE113 | DEAG_BW1165100000002 | DETP_BW1165100000002 | AICHWALD - AICHSCHIESS | 48.7544 | 9.4029 | 5200 | 5154 | NO | 32.2125 | 0 | 0 | 0 | 186.8325 | 1120.995 | DE11 | C
DE | DE113 | DEAG_BW1165100000004 | DETP_BW1165100000004 | BALTMANNSWEILER | 48.7497 | 9.4538 | 8000 | 4996 | NO | 31.225 | 0 | 0 | 0 | 181.105 | 1086.63 | DE11 | B
DE | DE113 | DEAG_BW1165100000006 | DETP_BW1165100000006 | DEIZISAU | 48.7152 | 9.3604 | 23300 | 10605 | NO | 66.2812 | 0 | 0 | 0 | 384.4312 | 2306.5875 | DE11 | A
DE | DE113 | DEAG_BW1165100000007 | DETP_BW1165100000007 | DENKENDORF | 48.6974 | 9.3356 | 15000 | 9431 | NO | 58.9438 | 0 | 0 | 0 | 341.8737 | 2051.2425 | DE11 | A
DE | DE113 | DEAG_BW1165100000009 | DETP_BW1165100000009 | FILDERSTADT - SIELMINGEN | 48.6798 | 9.2506 | 51100 | 28944 | YES | 180.9 | 578.88 | 434.16 | 868.32 | 1049.22 | 6295.32 | DE11 | B
DE | DE113 | DEAG_BW1165100000010 | DETP_BW1165100000010 | FILDERSTADT - BONLANDEN | 48.638 | 9.2192 | 27500 | 25301 | NO | 158.1312 | 0 | 0 | 0 | 917.1612 | 5502.9675 | DE11 | C
DE | DE113 | DEAG_BW1165100000011 | DETP_BW1165100000011 | GROSSBETTLINGEN | 48.5939 | 9.2976 | 6000 | 4285 | NO | 26.7812 | 0 | 0 | 0 | 155.3312 | 931.9875 | DE11 | B
DE | DE113 | DEAG_BW1165100000012 | DETP_BW1165100000012 | Kirchheim-Nabern | 48.6167 | 9.4716 | 7500 | 6011 | NO | 37.5688 | 0 | 0 | 0 | 217.8987 | 1307.3925 | DE11 | A
DE | DE113 | DEAG_BW1165100000013 | DETP_BW1165100000013 | LEINFELDEN-ECHTERDINGEN - STETTEN | 48.6754 | 9.1843 | 22600 | 15509 | NO | 96.9312 | 0 | 0 | 0 | 562.2012 | 3373.2075 | DE11 | A
DE | DE113 | DEAG_BW1165100000014 | DETP_BW1165100000014 | LEINFELDEN-ECHTERDINGEN - MUSBERG | 48.68 | 9.1264 | 11000 | 6726 | NO | 42.0375 | 0 | 0 | 0 | 243.8175 | 1462.905 | DE11 | C
DE | DE128 | DEAG_BW2265100000011 | DETP_BW2265100000011 | SKA AZV IM HOLLMUTH Bammental | 49.3635 | 8.789 | 39500 | 22114 | YES | 138.2125 | 442.28 | 331.71 | 663.42 | 801.6325 | 4809.795 | DE12 | B
DE | DE128 | DEAG_BW2265100000012 | DETP_BW2265100000012 | SKA AZV MECKESHEIMER CENT Meckesheim | 49.3328 | 8.8063 | 44000 | 20680 | YES | 129.25 | 413.6 | 310.2 | 620.4 | 749.65 | 4497.9 | DE12 | A
DE | DE128 | DEAG_BW2265100000013 | DETP_BW2265100000013 | SKA AZV SCHWARZBACHTAL Neckarbischofsheim | 49.3037 | 8.9409 | 35000 | 49170 | NO | 307.3125 | 0 | 0 | 0 | 1782.4125 | 10694.475 | DE12 | C
DE | DE128 | DEAG_BW2265100000014 | DETP_BW2265100000014 | SKA AZV WALDANGELBACHTAL Angelbachtal | 49.2398 | 8.7633 | 10000 | 10680 | NO | 66.75 | 0 | 0 | 0 | 387.15 | 2322.9 | DE12 | B
DE | DE128 | DEAG_BW2265100000015 | DETP_BW2265100000015 | SKA Eberbach | 49.4586 | 8.9579 | 28000 | 37606 | NO | 235.0375 | 0 | 0 | 0 | 1363.2175 | 8179.305 | DE12 | A
DE | DE128 | DEAG_BW2265100000016 | DETP_BW2265100000016 | SKA Hockenheim | 49.3299 | 8.5269 | 55000 | 40061 | YES | 250.3813 | 801.22 | 600.915 | 1201.83 | 1452.2113 | 8713.2675 | DE12 | A
DE | DE128 | DEAG_BW2265100000020 | DETP_BW2265100000020 | SKA Sinsheim | 49.256 | 8.86 | 75000 | 23514 | YES | 146.9625 | 470.28 | 352.71 | 705.42 | 852.3825 | 5114.295 | DE12 | A
DE | DE128 | DEAG_BW2265100000021 | DETP_BW2265100000021 | SKA Sinsheim-Hilsbach | 49.1859 | 8.862 | 7000 | 4014 | NO | 25.0875 | 0 | 0 | 0 | 145.5075 | 873.045 | DE12 | C
DE | DE128 | DEAG_BW2265100000024 | DETP_BW2265100000024 | SKA Waibstadt | 49.3032 | 8.9035 | 41500 | 41800 | YES | 261.25 | 836 | 627 | 1254 | 1515.25 | 9091.5 | DE12 | A
DE | DE128 | DEAG_BW2265100000025 | DETP_BW2265100000025 | SKA AV STEINACHTAL Schönau ( Hessen ) | 49.4141 | 8.8072 | 12500 | 4797 | NO | 29.9813 | 0 | 0 | 0 | 173.8913 | 1043.3475 | DE12 | A
DE | DE128 | DEAG_BW2265100000030 | DETP_BW2265100000030 | SKA St.Leon-Rot | 49.2789 | 8.6027 | 23500 | 14427 | NO | 90.1688 | 0 | 0 | 0 | 522.9787 | 3137.8725 | DE12 | B
DE | DE129 | DEAG_BW2315100000061 | DETP_BW2315100000061 | SKA PFORZHEIM | 48.9017 | 8.7351 | 250000 | 208128 | YES | 1300.8 | 4162.56 | 3121.92 | 6243.84 | 7544.64 | 45267.84 | DE12 | A
DE | DE12A | DEAG_BW2355100000003 | DETP_BW2355100000003 | SKA NAGOLD | 48.5677 | 8.7172 | 65000 | 39333 | YES | 245.8312 | 786.66 | 589.995 | 1179.99 | 1425.8212 | 8554.9275 | DE12 | B
DE | DE12A | DEAG_BW2355100000005 | DETP_BW2355100000005 | SKA BAD LIEBENZELL | 48.788 | 8.7266 | 20000 | 11413 | NO | 71.3312 | 0 | 0 | 0 | 413.7212 | 2482.3275 | DE12 | C
DE | DE12A | DEAG_BW2355100000019 | DETP_BW2355100000019 | SKA SIMMOZHEIM | 48.7492 | 8.8174 | 5600 | 6533 | NO | 40.8313 | 0 | 0 | 0 | 236.8212 | 1420.9275 | DE12 | A
DE | DE12A | DEAG_BW2355100000021 | DETP_BW2355100000021 | SKA WILDBERG | 48.6431 | 8.7367 | 23000 | 26924 | NO | 168.275 | 0 | 0 | 0 | 975.995 | 5855.97 | DE12 | C
DE | DE12A | DEAG_BW2355100000024 | DETP_BW2355100000024 | SKA CALMBACH | 48.7889 | 8.5776 | 30000 | 15236 | NO | 95.225 | 0 | 0 | 0 | 552.305 | 3313.83 | DE12 | A
DE | DE12A | DEAG_BW2355100000025 | DETP_BW2355100000025 | SKA UNTERREICHENBACH | 48.8325 | 8.7028 | 6500 | 3661 | NO | 22.8812 | 0 | 0 | 0 | 132.7112 | 796.2675 | DE12 | B
DE | DE12A | DEAG_BW2355100000026 | DETP_BW2355100000026 | SKA SCHÖMBERG CW | 48.7986 | 8.6587 | 25000 | 6510 | NO | 40.6875 | 0 | 0 | 0 | 235.9875 | 1415.925 | DE12 | C
DE | DE12A | DEAG_BW2355100000042 | DETP_BW2355100000042 | SKA GECHINGEN | 48.6979 | 8.8461 | 5000 | 3747 | NO | 23.4188 | 0 | 0 | 0 | 135.8288 | 814.9725 | DE12 | C
DE | DE12A | DEAG_BW2355100000048 | DETP_BW2355100000048 | SKA HIRSAU | 48.7452 | 8.7299 | 49500 | 37483 | YES | 234.2687 | 749.66 | 562.245 | 1124.49 | 1358.7587 | 8152.5525 | DE12 | A
DE | DE12A | DEAG_BW2355100000051 | DETP_BW2355100000051 | SKA BAD TEINACH | 48.6871 | 8.6996 | 6800 | 7072 | NO | 44.2 | 0 | 0 | 0 | 256.36 | 1538.16 | DE12 | B
DE | DE12A | DEAG_BW2355100000055 | DETP_BW2355100000055 | SKA ALTHENGSTETT | 48.7206 | 8.7766 | 18000 | 8439 | NO | 52.7438 | 0 | 0 | 0 | 305.9138 | 1835.4825 | DE12 | A
DE | DE12A | DEAG_BW2355100000057 | DETP_BW2355100000057 | SKA ALTENSTEIG | 48.5953 | 8.6252 | 34000 | 23908 | NO | 149.425 | 0 | 0 | 0 | 866.665 | 5199.99 | DE12 | A
DE | DE12B | DEAG_BW2365100000002 | DETP_BW2365100000002 | SKA ELLMENDINGEN | 48.9101 | 8.5646 | 28000 | 11882 | NO | 74.2625 | 0 | 0 | 0 | 430.7225 | 2584.335 | DE12 | C
DE | DE123 | DEAG_BW2365100000004 | DETP_BW2365100000004 | SKA KLEINSTEINBACH | 48.9696 | 8.5536 | 33000 | 15941 | NO | 99.6313 | 0 | 0 | 0 | 577.8612 | 3467.1675 | DE12 | A
DE | DE12B | DEAG_BW2365100000006 | DETP_BW2365100000006 | SKA KOENIGSBACH BB | 48.9596 | 8.5902 | 55000 | 28003 | YES | 175.0187 | 560.06 | 420.045 | 840.09 | 1015.1087 | 6090.6525 | DE12 | A
DE | DE12B | DEAG_BW2365100000010 | DETP_BW2365100000010 | SKA MÖNSHEIM | 48.8691 | 8.8787 | 7100 | 5028 | NO | 31.425 | 0 | 0 | 0 | 182.265 | 1093.59 | DE12 | C
DE | DE12B | DEAG_BW2365100000011 | DETP_BW2365100000011 | SKA SCHÜTZINGEN | 48.9933 | 8.9144 | 6700 | 5337 | NO | 33.3563 | 0 | 0 | 0 | 193.4663 | 1160.7975 | DE12 | C
DE | DE12B | DEAG_BW2365100000012 | DETP_BW2365100000012 | SKA GROSSGLATTBACH | 48.9147 | 8.9092 | 7500 | 5365 | NO | 33.5312 | 0 | 0 | 0 | 194.4812 | 1166.8875 | DE12 | C
DE | DE12B | DEAG_BW2365100000017 | DETP_BW2365100000017 | SKA TIEFENBRONN | 48.8316 | 8.7827 | 21000 | 14725 | NO | 92.0312 | 0 | 0 | 0 | 533.7812 | 3202.6875 | DE12 | C
DE | DE12B | DEAG_BW2365100000065 | DETP_BW2365100000065 | SKA NEUENBÜRG | 48.8527 | 8.6075 | 19500 | 12741 | NO | 79.6313 | 0 | 0 | 0 | 461.8613 | 2771.1675 | DE12 | C
DE | DE12B | DEAG_BW2365100000066 | DETP_BW2365100000066 | SKA NIEFERN | 48.9241 | 8.7913 | 25000 | 21750 | NO | 135.9375 | 0 | 0 | 0 | 788.4375 | 4730.625 | DE12 | B
DE | DE12B | DEAG_BW2365100000069 | DETP_BW2365100000069 | SKA Mühlacker-LOMERSHEIM | 48.9371 | 8.8742 | 40000 | 27912 | NO | 174.45 | 0 | 0 | 0 | 1011.81 | 6070.86 | DE12 | A
DE | DE12B | DEAG_BW2365100000071 | DETP_BW2365100000071 | SKA Mühlacker-ENZBERG | 48.9405 | 8.811 | 10000 | 5681 | NO | 35.5063 | 0 | 0 | 0 | 205.9363 | 1235.6175 | DE12 | A
DE | DE12B | DEAG_BW2365100000072 | DETP_BW2365100000072 | SKA ILLINGEN | 48.9464 | 8.9349 | 19800 | 5669 | NO | 35.4312 | 0 | 0 | 0 | 205.5012 | 1233.0075 | DE12 | B
DE | DE12B | DEAG_BW2365100000138 | DETP_BW2365100000138 | SKA FRIOLZHEIM Neu | 48.8244 | 8.8334 | 6250 | 5035 | NO | 31.4688 | 0 | 0 | 0 | 182.5187 | 1095.1125 | DE12 | C
DE | DE12C | DEAG_BW2375100000001 | DETP_BW2375100000001 | SKA VÖRBACH | 48.5143 | 8.5839 | 19000 | 16481 | NO | 103.0063 | 0 | 0 | 0 | 597.4362 | 3584.6175 | DE12 | C
DE | DE12C | DEAG_BW2375100000007 | DETP_BW2375100000007 | SKA GLATTEN | 48.4308 | 8.5162 | 22000 | 18741 | NO | 117.1313 | 0 | 0 | 0 | 679.3613 | 4076.1675 | DE12 | C
DE | DE12C | DEAG_BW2375100000013 | DETP_BW2375100000013 | SKA BAIERSBRONN | 48.5163 | 8.3839 | 38600 | 27214 | YES | 170.0875 | 544.28 | 408.21 | 816.42 | 986.5075 | 5919.045 | DE12 | A
DE | DE12C | DEAG_BW2375100000014 | DETP_BW2375100000014 | SKA AACH | 48.459 | 8.4819 | 25000 | 22734 | NO | 142.0875 | 0 | 0 | 0 | 824.1075 | 4944.645 | DE12 | B
DE | DE12C | DEAG_BW2375100000015 | DETP_BW2375100000015 | SKA EUTINGEN | 48.473 | 8.7403 | 16200 | 22776 | NO | 142.35 | 0 | 0 | 0 | 825.63 | 4953.78 | DE12 | A
DE | DE12C | DEAG_BW2375100000089 | DETP_BW2375100000089 | SKA DETTINGEN | 48.4205 | 8.6384 | 9000 | 9240 | NO | 57.75 | 0 | 0 | 0 | 334.95 | 2009.7 | DE12 | A
DE | DE12C | DEAG_BW2375100000092 | DETP_BW2375100000092 | SKA HORB | 48.4454 | 8.7115 | 28000 | 10513 | NO | 65.7062 | 0 | 0 | 0 | 381.0962 | 2286.5775 | DE12 | C
DE | DE12C | DEAG_BW2375100000100 | DETP_BW2375100000100 | SKA MANBACH | 48.4542 | 8.4384 | 23000 | 18321 | NO | 114.5063 | 0 | 0 | 0 | 664.1363 | 3984.8175 | DE12 | B
DE | DE12C | DEAG_BW2375100000103 | DETP_BW2375100000103 | SKA SCHÖNMÜNZACH | 48.6137 | 8.364 | 15000 | 10608 | NO | 66.3 | 0 | 0 | 0 | 384.54 | 2307.24 | DE12 | A
DE | DE12C | DEAG_BW2375100000107 | DETP_BW2375100000107 | SKA ALPIRSBACH | 48.3224 | 8.3943 | 30500 | 12916 | NO | 80.725 | 0 | 0 | 0 | 468.205 | 2809.23 | DE13 | C
DE | DE132 | DEAG_BW3155100000002 | DETP_BW3155100000002 | KA AZV WEILERTAL - NEUENBURG | 47.8243 | 7.562 | 62500 | 45213 | YES | 282.5813 | 904.26 | 678.195 | 1356.39 | 1638.9712 | 9833.8275 | DE13 | A
DE | DE132 | DEAG_BW3155100000003 | DETP_BW3155100000003 | KA AZV SULZBACH - GRISSHEIM | 47.8817 | 7.5882 | 40000 | 14026 | YES | 87.6625 | 280.52 | 210.39 | 420.78 | 508.4425 | 3050.655 | DE13 | C
DE | DE132 | DEAG_BW3155100000004 | DETP_BW3155100000004 | SKA AZV STAUFENER BUCHT-GREZHAUSEN | 47.9724 | 7.6347 | 114000 | 70873 | YES | 442.9563 | 1417.46 | 1063.095 | 2126.19 | 2569.1462 | 15414.8775 | DE13 | C
DE | DE132 | DEAG_BW3155100000006 | DETP_BW3155100000006 | KA AZV HASLACHTAL - LENZKIRCH | 47.8641 | 8.2247 | 17500 | 7553 | NO | 47.2063 | 0 | 0 | 0 | 273.7962 | 1642.7775 | DE13 | B
DE | DE132 | DEAG_BW3155100000009 | DETP_BW3155100000009 | KA VOGTSBURG - BURKHEIM | 48.1022 | 7.588 | 18000 | 13834 | NO | 86.4625 | 0 | 0 | 0 | 501.4825 | 3008.895 | DE13 | B
DE | DE132 | DEAG_BW3155100000011 | DETP_BW3155100000011 | KA TITISEE-NEUSTADT | 47.9021 | 8.237 | 54000 | 26349 | YES | 164.6813 | 526.98 | 395.235 | 790.47 | 955.1513 | 5730.9075 | DE13 | A
DE | DE132 | DEAG_BW3155100000019 | DETP_BW3155100000019 | KA SCHLUCHSEE-WOLFSGRUND | 47.8199 | 8.1623 | 8000 | 5131 | NO | 32.0688 | 0 | 0 | 0 | 185.9988 | 1115.9925 | DE13 | A
DE | DE132 | DEAG_BW3155100000031 | DETP_BW3155100000031 | KA LÖFFINGEN-SEPPENHOFEN | 47.8681 | 8.3595 | 9360 | 6535 | NO | 40.8438 | 0 | 0 | 0 | 236.8937 | 1421.3625 | DE13 | C
DE | DE132 | DEAG_BW3155100000036 | DETP_BW3155100000036 | KA HINTERZARTEN | 47.9109 | 8.0852 | 7350 | 6901 | NO | 43.1313 | 0 | 0 | 0 | 250.1612 | 1500.9675 | DE13 | B
DE | DE132 | DEAG_BW3155100000037 | DETP_BW3155100000037 | KA FRIEDENWEILER-RÖTENBACH | 47.8894 | 8.2873 | 5000 | 4593 | NO | 28.7063 | 0 | 0 | 0 | 166.4963 | 998.9775 | DE13 | A
DE | DE132 | DEAG_BW3155100000045 | DETP_BW3155100000045 | KA BREISACH AM RHEIN | 48.0494 | 7.5796 | 81000 | 31224 | YES | 195.15 | 624.48 | 468.36 | 936.72 | 1131.87 | 6791.22 | DE13 | A
DE | DE132 | DEAG_BW3155100000059 | DETP_BW3155100000059 | KA AZV HOHLEBACHTAL - STEINENSTADT | 47.7657 | 7.5358 | 16300 | 11905 | NO | 74.4062 | 0 | 0 | 0 | 431.5562 | 2589.3375 | DE13 | C
DE | DE132 | DEAG_BW3155100001667 | DETP_BW3155100001667 | KA BAD BELLINGEN | 47.7441 | 7.5483 | 15000 | 6677 | NO | 41.7313 | 0 | 0 | 0 | 242.0413 | 1452.2475 | DE13 | C
DE | DE133 | DEAG_BW3165100000005 | DETP_BW3165100000005 | SKA AZV UNTERE ELZ-KÖNDRINGEN | 48.1412 | 7.7821 | 91700 | 60929 | YES | 380.8063 | 1218.58 | 913.935 | 1827.87 | 2208.6762 | 13252.0575 | DE13 | C
DE | DE133 | DEAG_BW3165100000007 | DETP_BW3165100000007 | SKA AZV KAISERSTUHL NORD-WYHL | 48.1806 | 7.6495 | 14300 | 9203 | NO | 57.5188 | 0 | 0 | 0 | 333.6087 | 2001.6525 | DE13 | C
DE | DE133 | DEAG_BW3165100000008 | DETP_BW3165100000008 | SKA AZV BREISGAUER BUCHT - KA FORCHHEIM | 48.1893 | 7.7097 | 600000 | 524561 | YES | 3278.5063 | 10491.22 | 7868.415 | 15736.83 | 19015.3363 | 114092.0175 | DE13 | A
DE | DE133 | DEAG_BW3165100000012 | DETP_BW3165100000012 | SKA WINDEN-NIEDERWINDEN | 48.137 | 8.0101 | 5000 | 5540 | NO | 34.625 | 0 | 0 | 0 | 200.825 | 1204.95 | DE13 | C
DE | DE133 | DEAG_BW3165100000020 | DETP_BW3165100000020 | SKA SASBACH | 48.1445 | 7.6062 | 8000 | 3963 | NO | 24.7688 | 0 | 0 | 0 | 143.6587 | 861.9525 | DE13 | B
DE | DE133 | DEAG_BW3165100000021 | DETP_BW3165100000021 | SKA RHEINHAUSEN - NIEDERHAUSEN | 48.243 | 7.7111 | 5000 | 3651 | NO | 22.8187 | 0 | 0 | 0 | 132.3487 | 794.0925 | DE13 | A
DE | DE133 | DEAG_BW3165100000023 | DETP_BW3165100000023 | SKA Kenzingen | 48.2001 | 7.7561 | 13000 | 13343 | NO | 83.3937 | 0 | 0 | 0 | 483.6837 | 2902.1025 | DE13 | B
DE | DE133 | DEAG_BW3165100000025 | DETP_BW3165100000025 | SKA HERBOLZHEIM | 48.2261 | 7.7547 | 15000 | 8925 | NO | 55.7812 | 0 | 0 | 0 | 323.5312 | 1941.1875 | DE13 | A
DE | DE133 | DEAG_BW3165100000046 | DETP_BW3165100000046 | SKA ELZACH | 48.1669 | 8.0583 | 15000 | 10973 | NO | 68.5812 | 0 | 0 | 0 | 397.7713 | 2386.6275 | DE13 | A
DE | DE134 | DEAG_BW3175100000001 | DETP_BW3175100000001 | SKA AWV RAUM OFFENBURG | 48.5193 | 7.9152 | 200000 | 105989 | YES | 662.4312 | 2119.78 | 1589.835 | 3179.67 | 3842.1012 | 23052.6075 | DE13 | C
DE | DE134 | DEAG_BW3175100000002 | DETP_BW3175100000002 | SKA AWV RAUMSCHAFT LAHR | 48.3458 | 7.8232 | 100000 | 81846 | YES | 511.5375 | 1636.92 | 1227.69 | 2455.38 | 2966.9175 | 17801.505 | DE13 | A
DE | DE134 | DEAG_BW3175100000003 | DETP_BW3175100000003 | SKA KEHL | 48.6184 | 7.842 | 48000 | 52416 | YES | 327.6 | 1048.32 | 786.24 | 1572.48 | 1900.08 | 11400.48 | DE13 | C
DE | DE134 | DEAG_BW3175100000004 | DETP_BW3175100000004 | SKA AZV KINZIG HARMERSBACHTAL | 48.3517 | 8.0222 | 46100 | 43262 | YES | 270.3875 | 865.24 | 648.93 | 1297.86 | 1568.2475 | 9409.485 | DE13 | C
DE | DE134 | DEAG_BW3175100000005 | DETP_BW3175100000005 | SKA AWV VORDERES RENCHTAL | 48.6031 | 8.0069 | 28000 | 23192 | NO | 144.95 | 0 | 0 | 0 | 840.71 | 5044.26 | DE13 | C
DE | DE134 | DEAG_BW3175100000006 | DETP_BW3175100000006 | SKA AWV HAUSACH HORNBERG | 48.2838 | 8.1399 | 39600 | 41112 | YES | 256.95 | 822.24 | 616.68 | 1233.36 | 1490.31 | 8941.86 | DE13 | A
DE | DE134 | DEAG_BW3175100000007 | DETP_BW3175100000007 | SKA GENGENBACH | 48.4165 | 7.9918 | 33500 | 18581 | NO | 116.1313 | 0 | 0 | 0 | 673.5613 | 4041.3675 | DE13 | A
DE | DE134 | DEAG_BW3175100000008 | DETP_BW3175100000008 | SKA AWV SÜDLICHE ORTENAU | 48.3134 | 7.7459 | 64000 | 51285 | YES | 320.5312 | 1025.7 | 769.275 | 1538.55 | 1859.0812 | 11154.4875 | DE13 | C
DE | DE134 | DEAG_BW3175100000009 | DETP_BW3175100000009 | SKA AWV OBERES RENCHTAL | 48.4994 | 8.1376 | 24900 | 8912 | NO | 55.7 | 0 | 0 | 0 | 323.06 | 1938.36 | DE13 | C
DE | DE134 | DEAG_BW3175100000010 | DETP_BW3175100000010 | SKA ACHERN | 48.6378 | 8.0659 | 30200 | 23700 | NO | 148.125 | 0 | 0 | 0 | 859.125 | 5154.75 | DE13 | A
DE | DE134 | DEAG_BW3175100000011 | DETP_BW3175100000011 | SKA OBERKIRCH | 48.5415 | 8.0542 | 18000 | 23441 | NO | 146.5062 | 0 | 0 | 0 | 849.7362 | 5098.4175 | DE13 | C
DE | DE134 | DEAG_BW3175100000012 | DETP_BW3175100000012 | SKA APPENWEIER URLOFFEN | 48.5675 | 7.9652 | 12300 | 15705 | NO | 98.1562 | 0 | 0 | 0 | 569.3062 | 3415.8375 | DE13 | B
DE | DE134 | DEAG_BW3175100000013 | DETP_BW3175100000013 | SKA AWV FRIESENHEIM | 48.3961 | 7.8542 | 23950 | 18873 | NO | 117.9563 | 0 | 0 | 0 | 684.1463 | 4104.8775 | DE13 | C
DE | DE134 | DEAG_BW3175100000014 | DETP_BW3175100000014 | SKA AWV SASBACHTAL | 48.6647 | 8.0756 | 17000 | 14922 | NO | 93.2625 | 0 | 0 | 0 | 540.9225 | 3245.535 | DE13 | C
DE | DE134 | DEAG_BW3175100000015 | DETP_BW3175100000015 | SKA AWV ACHERTAL | 48.5985 | 8.1089 | 28400 | 25339 | NO | 158.3688 | 0 | 0 | 0 | 918.5388 | 5511.2325 | DE13 | A
DE | DE134 | DEAG_BW3175100000016 | DETP_BW3175100000016 | SKA AWV NEURIED SCHUTTERWALD | 48.4802 | 7.8035 | 25000 | 21663 | NO | 135.3938 | 0 | 0 | 0 | 785.2837 | 4711.7025 | DE13 | C
DE | DE134 | DEAG_BW3175100000018 | DETP_BW3175100000018 | SKA RHEINAU FREISTETT | 48.6843 | 7.949 | 13500 | 10653 | NO | 66.5812 | 0 | 0 | 0 | 386.1712 | 2317.0275 | DE13 | C
DE | DE134 | DEAG_BW3175100000019 | DETP_BW3175100000019 | SKA SCHWANAU SÜD -NONNENWEIER- | 48.3594 | 7.7506 | 6000 | 5771 | NO | 36.0688 | 0 | 0 | 0 | 209.1988 | 1255.1925 | DE13 | C
DE | DE135 | DEAG_BW3255100000006 | DETP_BW3255100000006 | SKA AICHHALDEN | 48.2609 | 8.398 | 5830 | 4841 | NO | 30.2562 | 0 | 0 | 0 | 175.4862 | 1052.9175 | DE13 | B
DE | DE135 | DEAG_BW3255100000007 | DETP_BW3255100000007 | SKA BERGFELDEN AV OBERES MÜHLBACHTAL | 48.3535 | 8.682 | 7600 | 8789 | NO | 54.9313 | 0 | 0 | 0 | 318.6012 | 1911.6075 | DE13 | B
DE | DE135 | DEAG_BW3255100000008 | DETP_BW3255100000008 | SKA BÖSINGEN | 48.2393 | 8.5668 | 6000 | 2825 | NO | 17.6562 | 0 | 0 | 0 | 102.4062 | 614.4375 | DE13 | A
DE | DE135 | DEAG_BW3255100000009 | DETP_BW3255100000009 | SKA BÖHRINGEN AZV UNTERES SCHLICHEMTAL | 48.239 | 8.655 | 8400 | 4148 | NO | 25.925 | 0 | 0 | 0 | 150.365 | 902.19 | DE13 | B
DE | DE135 | DEAG_BW3255100000011 | DETP_BW3255100000011 | SKA FISCHINGEN, AV EMPFINGEN | 48.3967 | 8.6656 | 8100 | 6886 | NO | 43.0375 | 0 | 0 | 0 | 249.6175 | 1497.705 | DE13 | C
DE | DE135 | DEAG_BW3255100000013 | DETP_BW3255100000013 | SKA GLATT AV UNTERES GLATTAL | 48.3955 | 8.6419 | 10500 | 8895 | NO | 55.5938 | 0 | 0 | 0 | 322.4437 | 1934.6625 | DE13 | C
DE | DE135 | DEAG_BW3255100000015 | DETP_BW3255100000015 | SKA HORGEN ZVA ESCHACHTAL | 48.1371 | 8.5645 | 32000 | 36290 | NO | 226.8125 | 0 | 0 | 0 | 1315.5125 | 7893.075 | DE13 | C
DE | DE135 | DEAG_BW3255100000017 | DETP_BW3255100000017 | SKA NEUFRA | 48.1335 | 8.656 | 39000 | 34113 | NO | 213.2062 | 0 | 0 | 0 | 1236.5962 | 7419.5775 | DE13 | C
DE | DE135 | DEAG_BW3255100000018 | DETP_BW3255100000018 | SKA ROTTWEIL | 48.1729 | 8.635 | 52000 | 48277 | YES | 301.7312 | 965.54 | 724.155 | 1448.31 | 1750.0412 | 10500.2475 | DE13 | A
DE | DE135 | DEAG_BW3255100000020 | DETP_BW3255100000020 | SKA SCHILTACH OBERES KINZIGTAL | 48.2936 | 8.3066 | 15000 | 6107 | NO | 38.1688 | 0 | 0 | 0 | 221.3788 | 1328.2725 | DE13 | C
DE | DE135 | DEAG_BW3255100000021 | DETP_BW3255100000021 | SKA SULZ | 48.3682 | 8.6445 | 10500 | 13041 | NO | 81.5063 | 0 | 0 | 0 | 472.7363 | 2836.4175 | DE13 | A
DE | DE135 | DEAG_BW3255100000022 | DETP_BW3255100000022 | SKA SCHRAMBERG | 48.2451 | 8.3756 | 41400 | 22602 | YES | 141.2625 | 452.04 | 339.03 | 678.06 | 819.3225 | 4915.935 | DE13 | C
DE | DE135 | DEAG_BW3255100000026 | DETP_BW3255100000026 | SKA VILLINGENDORF | 48.2023 | 8.5945 | 6000 | 2608 | NO | 16.3 | 0 | 0 | 0 | 94.54 | 567.24 | DE13 | A
DE | DE135 | DEAG_BW3255100000056 | DETP_BW3255100000056 | SKA AISTAIG | 48.3203 | 8.5858 | 35500 | 24428 | NO | 152.675 | 0 | 0 | 0 | 885.515 | 5313.09 | DE13 | C
DE | DE135 | DEAG_BW3255100000057 | DETP_BW3255100000057 | SKA DEISSLINGEN AZV OBERER NECKAR VS | 48.0875 | 8.5815 | 75000 | 59268 | YES | 370.425 | 1185.36 | 889.02 | 1778.04 | 2148.465 | 12890.79 | DE13 | B
DE | DE136 | DEAG_BW3265100000001 | DETP_BW3265100000001 | SKA Villingen | 48.0412 | 8.4679 | 70500 | 53534 | YES | 334.5875 | 1070.68 | 803.01 | 1606.02 | 1940.6075 | 11643.645 | DE13 | A
DE | DE136 | DEAG_BW3265100000002 | DETP_BW3265100000002 | SKA St. Georgen-Peterzell | 48.1238 | 8.3859 | 24000 | 14110 | NO | 88.1875 | 0 | 0 | 0 | 511.4875 | 3068.925 | DE13 | A
DE | DE136 | DEAG_BW3265100000003 | DETP_BW3265100000003 | SKA Furtwangen | 48.0466 | 8.2207 | 17500 | 15004 | NO | 93.775 | 0 | 0 | 0 | 543.895 | 3263.37 | DE13 | A
DE | DE136 | DEAG_BW3265100000004 | DETP_BW3265100000004 | SKA Blumberg-Achdorf | 47.8314 | 8.5057 | 25800 | 17520 | NO | 109.5 | 0 | 0 | 0 | 635.1 | 3810.6 | DE13 | C
DE | DE136 | DEAG_BW3265100000013 | DETP_BW3265100000013 | SKA Triberg-Gremmelsbach | 48.1612 | 8.2377 | 16000 | 22190 | NO | 138.6875 | 0 | 0 | 0 | 804.3875 | 4826.325 | DE13 | C
DE | DE136 | DEAG_BW3265100000014 | DETP_BW3265100000014 | SKA Hammereisenbach | 47.9935 | 8.3461 | 7000 | 5521 | NO | 34.5063 | 0 | 0 | 0 | 200.1363 | 1200.8175 | DE13 | C
DE | DE136 | DEAG_BW3265100000015 | DETP_BW3265100000015 | SKA Unterbaldingen | 47.9578 | 8.6182 | 9500 | 6933 | NO | 43.3313 | 0 | 0 | 0 | 251.3213 | 1507.9275 | DE13 | C
DE | DE136 | DEAG_BW3265100000016 | DETP_BW3265100000016 | SKA Donaueschingen | 47.9498 | 8.5227 | 120000 | 89019 | YES | 556.3687 | 1780.38 | 1335.285 | 2670.57 | 3226.9387 | 19361.6325 | DE13 | A
DE | DE137 | DEAG_BW3275100000030 | DETP_BW3275100000030 | SKA Egesheim GVV Heuberg | 48.1115 | 8.867 | 19100 | 13026 | NO | 81.4125 | 0 | 0 | 0 | 472.1925 | 2833.155 | DE13 | C
DE | DE137 | DEAG_BW3275100000031 | DETP_BW3275100000031 | SKA Emmingen | 47.9363 | 8.8677 | 7500 | 6181 | NO | 38.6313 | 0 | 0 | 0 | 224.0613 | 1344.3675 | DE13 | A
DE | DE137 | DEAG_BW3275100000033 | DETP_BW3275100000033 | SKA Fridingen | 48.0125 | 8.9209 | 5300 | 2514 | NO | 15.7125 | 0 | 0 | 0 | 91.1325 | 546.795 | DE13 | B
DE | DE137 | DEAG_BW3275100000034 | DETP_BW3275100000034 | SKA Immendingen GVV Immendingen-Geisingen | 47.9328 | 8.7471 | 25500 | 11940 | NO | 74.625 | 0 | 0 | 0 | 432.825 | 2596.95 | DE13 | B
DE | DE137 | DEAG_BW3275100000039 | DETP_BW3275100000039 | SKA Möhringen | 47.9692 | 8.7851 | 7500 | 5644 | NO | 35.275 | 0 | 0 | 0 | 204.595 | 1227.57 | DE13 | A
DE | DE137 | DEAG_BW3275100000040 | DETP_BW3275100000040 | SKA Mühlheim | 48.0336 | 8.8945 | 11000 | 6550 | NO | 40.9375 | 0 | 0 | 0 | 237.4375 | 1424.625 | DE13 | B
DE | DE137 | DEAG_BW3275100000045 | DETP_BW3275100000045 | SKA Spaichingen | 48.0876 | 8.7263 | 23000 | 21854 | NO | 136.5875 | 0 | 0 | 0 | 792.2075 | 4753.245 | DE13 | B
DE | DE137 | DEAG_BW3275100000046 | DETP_BW3275100000046 | SKA Seitingen AZV Ostbaar | 48.0127 | 8.7311 | 7000 | 4421 | NO | 27.6312 | 0 | 0 | 0 | 160.2612 | 961.5675 | DE13 | B
DE | DE137 | DEAG_BW3275100000048 | DETP_BW3275100000048 | SKA Trossingen | 48.081 | 8.6534 | 21700 | 17902 | NO | 111.8875 | 0 | 0 | 0 | 648.9475 | 3893.685 | DE13 | A
DE | DE137 | DEAG_BW3275100000049 | DETP_BW3275100000049 | SKA Tuttlingen | 48.0027 | 8.8397 | 75000 | 43433 | YES | 271.4563 | 868.66 | 651.495 | 1302.99 | 1574.4462 | 9446.6775 | DE13 | B
DE | DE137 | DEAG_BW3275100000050 | DETP_BW3275100000050 | SKA Weilheim GKW Faulenbachtal | 48.0195 | 8.7769 | 7500 | 4492 | NO | 28.075 | 0 | 0 | 0 | 162.835 | 977.01 | DE13 | B
DE | DE138 | DEAG_BW3355100000005 | DETP_BW3355100000005 | SKA Konstanz | 47.6778 | 9.142 | 215000 | 168417 | YES | 1052.6063 | 3368.34 | 2526.255 | 5052.51 | 6105.1163 | 36630.6975 | DE13 | A
DE | DE138 | DEAG_BW3355100000016 | DETP_BW3355100000016 | SKA Gailingen | 47.6934 | 8.7501 | 5700 | 2531 | NO | 15.8188 | 0 | 0 | 0 | 91.7488 | 550.4925 | DE13 | A
DE | DE138 | DEAG_BW3355100000017 | DETP_BW3355100000017 | SKA Steisslingen | 47.7811 | 8.9276 | 6000 | 3811 | NO | 23.8187 | 0 | 0 | 0 | 138.1487 | 828.8925 | DE13 | A
DE | DE138 | DEAG_BW3355100000019 | DETP_BW3355100000019 | VKA Stockacher Aach | 47.815 | 9.0227 | 69000 | 43023 | YES | 268.8938 | 860.46 | 645.345 | 1290.69 | 1559.5837 | 9357.5025 | DE13 | C
DE | DE138 | DEAG_BW3355100000020 | DETP_BW3355100000020 | VKA Untere Radolfzeller Aach/Moos | 47.7174 | 8.9387 | 20000 | 15699 | NO | 98.1187 | 0 | 0 | 0 | 569.0887 | 3414.5325 | DE13 | B
DE | DE138 | DEAG_BW3355100000021 | DETP_BW3355100000021 | SKA Gaienhofen | 47.6814 | 8.9849 | 7350 | 7536 | NO | 47.1 | 0 | 0 | 0 | 273.18 | 1639.08 | DE13 | A
DE | DE139 | DEAG_BW3365100000001 | DETP_BW3365100000001 | SKA BÄNDLEGRUND | 47.6152 | 7.5822 | 290000 | 109786 | YES | 686.1625 | 2195.72 | 1646.79 | 3293.58 | 3979.7425 | 23878.455 | DE13 | A
DE | DE139 | DEAG_BW3365100000003 | DETP_BW3365100000003 | SKA STEINEN | 47.6388 | 7.7361 | 75000 | 46302 | YES | 289.3875 | 926.04 | 694.53 | 1389.06 | 1678.4475 | 10070.685 | DE13 | A
DE | DE139 | DEAG_BW3365100000012 | DETP_BW3365100000012 | SKA WEMBACH | 47.7719 | 7.888 | 14200 | 7585 | NO | 47.4062 | 0 | 0 | 0 | 274.9562 | 1649.7375 | DE13 | A
DE | DE139 | DEAG_BW3365100000013 | DETP_BW3365100000013 | SKA RHEINFELDEN | 47.5457 | 7.7469 | 47000 | 36738 | YES | 229.6125 | 734.76 | 551.07 | 1102.14 | 1331.7525 | 7990.515 | DE13 | A
DE | DE139 | DEAG_BW3365100000016 | DETP_BW3365100000016 | SKA KANDERN-HAMMERSTEIN | 47.6866 | 7.6428 | 10000 | 5202 | NO | 32.5125 | 0 | 0 | 0 | 188.5725 | 1131.435 | DE13 | C
DE | DE139 | DEAG_BW3365100000021 | DETP_BW3365100000021 | SKA TODTNAU | 47.8125 | 7.9371 | 18000 | 9710 | NO | 60.6875 | 0 | 0 | 0 | 351.9875 | 2111.925 | DE13 | C
DE | DE139 | DEAG_BW3365100000023 | DETP_BW3365100000023 | SKA SCHWÖRSTADT | 47.5887 | 7.8572 | 13660 | 7614 | NO | 47.5875 | 0 | 0 | 0 | 276.0075 | 1656.045 | DE13 | C
DE | DE13A | DEAG_BW3375100000010 | DETP_BW3375100000010 | SKA Bonndorf | 47.7819 | 8.4007 | 10300 | 8830 | NO | 55.1875 | 0 | 0 | 0 | 320.0875 | 1920.525 | DE13 | C
DE | DE13A | DEAG_BW3375100000034 | DETP_BW3375100000034 | SKA Hohentengen | 47.5736 | 8.4115 | 16000 | 15303 | NO | 95.6438 | 0 | 0 | 0 | 554.7338 | 3328.4025 | DE13 | C
DE | DE13A | DEAG_BW3375100000037 | DETP_BW3375100000037 | SKA Jestetten | 47.6514 | 8.6031 | 6400 | 5949 | NO | 37.1812 | 0 | 0 | 0 | 215.6512 | 1293.9075 | DE13 | B
DE | DE13A | DEAG_BW3375100000038 | DETP_BW3375100000038 | SKA Klettgau- OTGeißlingen | 47.6145 | 8.3822 | 7000 | 5746 | NO | 35.9125 | 0 | 0 | 0 | 208.2925 | 1249.755 | DE13 | C
DE | DE143 | DEAG_BW4175100000008 | DETP_BW4175100000008 | SKA Karlstal (Haigerloch) | 48.3803 | 8.7923 | 12500 | 12378 | NO | 77.3625 | 0 | 0 | 0 | 448.7025 | 2692.215 | DE14 | C
DE | DE143 | DEAG_BW4175100000010 | DETP_BW4175100000010 | SKA Hechingen | 48.3683 | 8.9534 | 57200 | 38936 | YES | 243.35 | 778.72 | 584.04 | 1168.08 | 1411.43 | 8468.58 | DE14 | B
DE | DE143 | DEAG_BW4175100000011 | DETP_BW4175100000011 | SKA Unterdigisheim (Meßstetten) | 48.1521 | 8.9042 | 12000 | 8541 | NO | 53.3813 | 0 | 0 | 0 | 309.6112 | 1857.6675 | DE14 | C
DE | DE143 | DEAG_BW4175100000013 | DETP_BW4175100000013 | SKA Rangendingen | 48.3894 | 8.873 | 6000 | 5870 | NO | 36.6875 | 0 | 0 | 0 | 212.7875 | 1276.725 | DE14 | C
DE | DE143 | DEAG_BW4175100000014 | DETP_BW4175100000014 | SKA Bietenhausen (Rangend.) des AZV Starzeltal Hirrlingen | 48.4132 | 8.8694 | 5000 | 4557 | NO | 28.4813 | 0 | 0 | 0 | 165.1912 | 991.1475 | DE14 | C
DE | DE143 | DEAG_BW4175100000015 | DETP_BW4175100000015 | SKA Rosenfeld | 48.2902 | 8.7449 | 6500 | 5879 | NO | 36.7437 | 0 | 0 | 0 | 213.1137 | 1278.6825 | DE14 | B
DE | DE143 | DEAG_BW4175100000019 | DETP_BW4175100000019 | SKA Schömberg des GVV Oberes Schlichemtal | 48.2226 | 8.7639 | 6500 | 11153 | NO | 69.7062 | 0 | 0 | 0 | 404.2962 | 2425.7775 | DE14 | C
DE | DE143 | DEAG_BW4175100000020 | DETP_BW4175100000020 | SKA Kaiseringen (Straßberg) des AZV Schmeietal | 48.1545 | 9.1058 | 16000 | 7730 | NO | 48.3125 | 0 | 0 | 0 | 280.2125 | 1681.275 | DE14 | C
DE | DE143 | DEAG_BW4175100000021 | DETP_BW4175100000021 | SKA Lautlingen (Albstadt) des AZV Oberes Eyachtal | 48.2157 | 8.9415 | 36000 | 13119 | NO | 81.9938 | 0 | 0 | 0 | 475.5638 | 2853.3825 | DE14 | A
DE | DE143 | DEAG_BW4175100000023 | DETP_BW4175100000023 | SKA Balingen des ZVA Balingen | 48.2965 | 8.8593 | 124000 | 61039 | YES | 381.4938 | 1220.78 | 915.585 | 1831.17 | 2212.6638 | 13275.9825 | DE14 | B
DE | DE143 | DEAG_BW4175100000024 | DETP_BW4175100000024 | SKA Ebingen (Albstadt) | 48.1993 | 9.0513 | 125000 | 55482 | YES | 346.7625 | 1109.64 | 832.23 | 1664.46 | 2011.2225 | 12067.335 | DE14 | A
DE | DE145 | DEAG_BW4255100000001 | DETP_BW4255100000001 | SKA Halzhausen | 48.5304 | 9.9298 | 16000 | 19857 | NO | 124.1063 | 0 | 0 | 0 | 719.8162 | 4318.8975 | DE14 | B
DE | DE145 | DEAG_BW4255100000009 | DETP_BW4255100000009 | SKA Öpfingen | 48.2863 | 9.8139 | 6000 | 5579 | NO | 34.8687 | 0 | 0 | 0 | 202.2387 | 1213.4325 | DE14 | B
DE | DE145 | DEAG_BW4255100000012 | DETP_BW4255100000012 | SKA Schelklingen | 48.3788 | 9.7495 | 10000 | 7980 | NO | 49.875 | 0 | 0 | 0 | 289.275 | 1735.65 | DE14 | A
DE | DE145 | DEAG_BW4255100000014 | DETP_BW4255100000014 | SKA Rottenacker | 48.237 | 9.7048 | 25000 | 21123 | NO | 132.0188 | 0 | 0 | 0 | 765.7088 | 4594.2525 | DE14 | B
DE | DE145 | DEAG_BW4255100000017 | DETP_BW4255100000017 | SKA Westerheim | 48.5064 | 9.6133 | 5500 | 3678 | NO | 22.9875 | 0 | 0 | 0 | 133.3275 | 799.965 | DE14 | B
DE | DE145 | DEAG_BW4255100000021 | DETP_BW4255100000021 | SKA Bernstadt | 48.5095 | 10.0116 | 6000 | 4290 | NO | 26.8125 | 0 | 0 | 0 | 155.5125 | 933.075 | DE14 | C
DE | DE145 | DEAG_BW4255100000022 | DETP_BW4255100000022 | SKA Blaubeuren-Gerhausen | 48.397 | 9.8145 | 14500 | 8523 | NO | 53.2688 | 0 | 0 | 0 | 308.9588 | 1853.7525 | DE14 | A
DE | DE145 | DEAG_BW4255100000023 | DETP_BW4255100000023 | SKA Ehingen | 48.2717 | 9.733 | 45000 | 38735 | YES | 242.0938 | 774.7 | 581.025 | 1162.05 | 1404.1437 | 8424.8625 | DE14 | A
DE | DE145 | DEAG_BW4255100000027 | DETP_BW4255100000027 | SKA Erbach | 48.3257 | 9.9063 | 25000 | 18924 | NO | 118.275 | 0 | 0 | 0 | 685.995 | 4115.97 | DE14 | A
DE | DE145 | DEAG_BW4255100000028 | DETP_BW4255100000028 | SKA Heroldstatt | 48.4418 | 9.6791 | 7100 | 3306 | NO | 20.6625 | 0 | 0 | 0 | 119.8425 | 719.055 | DE14 | B
DE | DE145 | DEAG_BW4255100000029 | DETP_BW4255100000029 | SKA Laichingen | 48.4941 | 9.7035 | 35000 | 25365 | NO | 158.5312 | 0 | 0 | 0 | 919.4812 | 5516.8875 | DE14 | A
DE | DE145 | DEAG_BW4255100000031 | DETP_BW4255100000031 | SKA Langenau | 48.4997 | 10.14 | 16600 | 14715 | NO | 91.9688 | 0 | 0 | 0 | 533.4187 | 3200.5125 | DE14 | A
DE | DE146 | DEAG_BW4265100000001 | DETP_BW4265100000001 | SKA TANNHEIM | 48.0115 | 10.1149 | 13300 | 13845 | NO | 86.5312 | 0 | 0 | 0 | 501.8813 | 3011.2875 | DE14 | C
DE | DE124 | DEAG_BW2165100000012 | DETP_BW2165100000012 | KLA RASTATT AV MURG | 48.8836 | 8.2007 | 140000 | 131714 | YES | 823.2125 | 2634.28 | 1975.71 | 3951.42 | 4774.6325 | 28647.795 | DE12 | C
DE | DE124 | DEAG_BW2165100000013 | DETP_BW2165100000013 | AV SCHWARZWASSER KLA LICHTENAU | 48.7388 | 7.9916 | 19000 | 10125 | NO | 63.2812 | 0 | 0 | 0 | 367.0312 | 2202.1875 | DE12 | C
DE | DE124 | DEAG_BW2165100000039 | DETP_BW2165100000039 | KLA Forbach Bermersbach | 48.7011 | 8.3516 | 7000 | 3017 | NO | 18.8562 | 0 | 0 | 0 | 109.3662 | 656.1975 | DE12 | C
DE | DE124 | DEAG_BW2165100000040 | DETP_BW2165100000040 | KLA IFFEZHEIM | 48.8301 | 8.1435 | 11500 | 5952 | NO | 37.2 | 0 | 0 | 0 | 215.76 | 1294.56 | DE12 | B
DE | DE125 | DEAG_BW2215100000002 | DETP_BW2215100000002 | SKA AZV HEIDELBERG | 49.435 | 8.6519 | 360000 | 215042 | YES | 1344.0125 | 4300.84 | 3225.63 | 6451.26 | 7795.2725 | 46771.635 | DE12 | B
DE | DE126 | DEAG_BW2225100000001 | DETP_BW2225100000001 | Kläranlage Mannheim | 49.5655 | 8.4257 | 725000 | 517255 | YES | 3232.8438 | 10345.1 | 7758.825 | 15517.65 | 18750.4937 | 112502.9625 | DE12 | A
DE | DE127 | DEAG_BW2255100000005 | DETP_BW2255100000005 | SKA BCH-Buchen | 49.5332 | 9.3096 | 28000 | 7248 | NO | 45.3 | 0 | 0 | 0 | 262.74 | 1576.44 | DE12 | C
DE | DE127 | DEAG_BW2255100000010 | DETP_BW2255100000010 | SKA HSH-Haßmersheim | 49.3131 | 9.1374 | 6000 | 4731 | NO | 29.5687 | 0 | 0 | 0 | 171.4987 | 1028.9925 | DE12 | A
DE | DE127 | DEAG_BW2255100000017 | DETP_BW2255100000017 | Mudau-Donebach | 49.547 | 9.2091 | 5380 | 10963 | NO | 68.5187 | 0 | 0 | 0 | 397.4087 | 2384.4525 | DE12 | C
DE | DE127 | DEAG_BW2255100000031 | DETP_BW2255100000031 | SKA WAD-Walldürn | 49.5953 | 9.3542 | 15000 | 10000 | NO | 62.5 | 0 | 0 | 0 | 362.5 | 2175 | DE12 | B
DE | DE127 | DEAG_BW2255100000042 | DETP_BW2255100000042 | SKA HDH-Hardheim | 49.6223 | 9.4477 | 30000 | 32440 | NO | 202.75 | 0 | 0 | 0 | 1175.95 | 7055.7 | DE12 | C
DE | DE127 | DEAG_BW2255100000043 | DETP_BW2255100000043 | SKA BIL-Allfeld Schefflenztal | 49.3092 | 9.2465 | 19000 | 10251 | NO | 64.0688 | 0 | 0 | 0 | 371.5987 | 2229.5925 | DE12 | C
DE | DE127 | DEAG_BW2255100000044 | DETP_BW2255100000044 | SKA OBH-Obrigheim Elz-Neckar | 49.366 | 9.0832 | 70000 | 23508 | YES | 146.925 | 470.16 | 352.62 | 705.24 | 852.165 | 5112.99 | DE12 | B
DE | DE127 | DEAG_BW2255100000045 | DETP_BW2255100000045 | SKA FAB-Fahrenbach | 49.4261 | 9.1675 | 6000 | 2044 | NO | 12.775 | 0 | 0 | 0 | 74.095 | 444.57 | DE12 | C
DE | DE128 | DEAG_BW2265100000005 | DETP_BW2265100000005 | SKA AV BERGSTRASSE Weinheim | 49.5659 | 8.6147 | 200000 | 179206 | YES | 1120.0375 | 3584.12 | 2688.09 | 5376.18 | 6496.2175 | 38977.305 | DE12 | C
DE | DE128 | DEAG_BW2265100000006 | DETP_BW2265100000006 | SKA AHW WIESLOCH | 49.3027 | 8.6687 | 110000 | 89745 | YES | 560.9062 | 1794.9 | 1346.175 | 2692.35 | 3253.2562 | 19519.5375 | DE12 | A
DE | DE128 | DEAG_BW2265100000007 | DETP_BW2265100000007 | SKA ZV BEZIRK SCHWETZINGEN Ketsch | 49.3838 | 8.5257 | 120000 | 90681 | YES | 566.7563 | 1813.62 | 1360.215 | 2720.43 | 3287.1862 | 19723.1175 | DE12 | B
DE | DE128 | DEAG_BW2265100000008 | DETP_BW2265100000008 | SKA AZV UNTERE HARDT St.Ilgen | 49.3513 | 8.6653 | 125000 | 75245 | YES | 470.2812 | 1504.9 | 1128.675 | 2257.35 | 2727.6312 | 16365.7875 | DE12 | B
DE | DE128 | DEAG_BW2265100000009 | DETP_BW2265100000009 | SKA AV UNTERER NECKAR Neckarhausen | 49.4744 | 8.581 | 80000 | 63133 | YES | 394.5813 | 1262.66 | 946.995 | 1893.99 | 2288.5712 | 13731.4275 | DE12 | B
DE | DE147 | DEAG_BW4355100000012 | DETP_BW4355100000012 | SKA Friedrichshafen | 47.6487 | 9.5072 | 87000 | 63897 | YES | 399.3563 | 1277.94 | 958.455 | 1916.91 | 2316.2663 | 13897.5975 | DE14 | A
DE | DE147 | DEAG_BW4355100000030 | DETP_BW4355100000030 | SKA OBERTEURINGEN | 47.7102 | 9.4624 | 5700 | 5691 | NO | 35.5688 | 0 | 0 | 0 | 206.2987 | 1237.7925 | DE14 | C
DE | DE147 | DEAG_BW4355100000032 | DETP_BW4355100000032 | SKA UNTERSIGGINGEN | 47.7769 | 9.3709 | 8000 | 8341 | NO | 52.1313 | 0 | 0 | 0 | 302.3612 | 1814.1675 | DE14 | B
DE | DE148 | DEAG_BW4365100000015 | DETP_BW4365100000015 | SKA HASLACHMÜHLE | 47.8202 | 9.4602 | 13200 | 8262 | NO | 51.6375 | 0 | 0 | 0 | 299.4975 | 1796.985 | DE14 | C
DE | DE148 | DEAG_BW4365100000019 | DETP_BW4365100000019 | SKA WANGEN I.A. | 47.6543 | 9.7417 | 86500 | 49167 | YES | 307.2937 | 983.34 | 737.505 | 1475.01 | 1782.3037 | 10693.8225 | DE14 | C
DE | DE148 | DEAG_BW4365100000020 | DETP_BW4365100000020 | SKA LEUTKIRCH | 47.8435 | 10.0084 | 100000 | 91654 | YES | 572.8375 | 1833.08 | 1374.81 | 2749.62 | 3322.4575 | 19934.745 | DE14 | A
DE | DE275 | DEAG_BYDON-K0163 | DETP_BYDON-K0163 | Friedberg-Nord | 48.4208 | 10.9447 | 10000 | 5515 | NO | 34.4688 | 0 | 0 | 0 | 199.9187 | 1199.5125 | DE27 | C
DE | DE275 | DEAG_BYDON-K0164 | DETP_BYDON-K0164 | Aichach | 49.7707 | 10.153 | 35000 | 44230 | NO | 276.4375 | 0 | 0 | 0 | 1603.3375 | 9620.025 | DE26 | A
DE | DE27D | DEAG_BYDON-K0169 | DETP_BYDON-K0169 | AZV Mittlere Wörnitz | 48.8526 | 10.658 | 20000 | 14877 | NO | 92.9813 | 0 | 0 | 0 | 539.2912 | 3235.7475 | DE27 | C
DE | DE277 |  | DETP_BYDON-K0170 | ZV Härtsfeld-Württemberg | 48.6639 | 10.3905 | 25000 | 23838 | NO | 148.9875 | 0 | 0 | 0 | 864.1275 | 5184.765 | DE27 | C
DE | DE148 | DEAG_BW4365100000024 | DETP_BW4365100000024 | SKA ETTISHOFEN | 47.8235 | 9.6126 | 25000 | 16102 | YES | 100.6375 | 322.04 | 241.53 | 483.06 | 583.6975 | 3502.185 | DE14 | B
DE | DE148 | DEAG_BW4365100000025 | DETP_BW4365100000025 | SKA LANGWIESE | 47.7478 | 9.5765 | 184000 | 238961 | YES | 1493.5063 | 4779.22 | 3584.415 | 7168.83 | 8662.3363 | 51974.0175 | DE14 | A
DE | DE148 | DEAG_BW4365100000026 | DETP_BW4365100000026 | SKA VOGT | 47.7597 | 9.7722 | 9200 | 9497 | NO | 59.3562 | 0 | 0 | 0 | 344.2662 | 2065.5975 | DE14 | C
DE | DE148 | DEAG_BW4365100000027 | DETP_BW4365100000027 | SKA BODNEGG | 47.7132 | 9.6681 | 6000 | 6182 | NO | 38.6375 | 0 | 0 | 0 | 224.0975 | 1344.585 | DE14 | C
DE | DE148 | DEAG_BW4365100000029 | DETP_BW4365100000029 | SKA SCHLIER | 47.7866 | 9.6579 | 9500 | 6673 | NO | 41.7063 | 0 | 0 | 0 | 241.8963 | 1451.3775 | DE14 | C
DE | DE148 | DEAG_BW4365100000035 | DETP_BW4365100000035 | SKA REUTE | 47.8986 | 9.6917 | 8000 | 3942 | NO | 24.6375 | 0 | 0 | 0 | 142.8975 | 857.385 | DE14 | A
DE | DE148 | DEAG_BW4365100000038 | DETP_BW4365100000038 | SKA KISSLEGG | 47.7778 | 9.8876 | 19500 | 14056 | NO | 87.85 | 0 | 0 | 0 | 509.53 | 3057.18 | DE14 | B
DE | DE148 | DEAG_BW4365100000040 | DETP_BW4365100000040 | SKA AULENDORF | 47.9321 | 9.6451 | 19000 | 9757 | NO | 60.9812 | 0 | 0 | 0 | 353.6912 | 2122.1475 | DE14 | B
DE | DE148 | DEAG_BW4365100000042 | DETP_BW4365100000042 | SKA BAD WALDSEE | 47.9162 | 9.7217 | 25000 | 15396 | NO | 96.225 | 0 | 0 | 0 | 558.105 | 3348.63 | DE14 | C
DE | DE148 | DEAG_BW4365100000043 | DETP_BW4365100000043 | SKA BAD WURZACH | 47.8851 | 9.9108 | 25000 | 15051 | NO | 94.0688 | 0 | 0 | 0 | 545.5987 | 3273.5925 | DE14 | C
DE | DE148 | DEAG_BW4365100000044 | DETP_BW4365100000044 | SKA BERGATREUTE | 47.8476 | 9.7218 | 5000 | 3111 | NO | 19.4438 | 0 | 0 | 0 | 112.7737 | 676.6425 | DE14 | C
DE | DE148 | DEAG_BW4365100000045 | DETP_BW4365100000045 | SKA DÜRREN | 47.7346 | 9.8888 | 8350 | 5857 | NO | 36.6063 | 0 | 0 | 0 | 212.3163 | 1273.8975 | DE14 | C
DE | DE148 | DEAG_BW4365100000049 | DETP_BW4365100000049 | SKA ALTSHAUSEN | 47.9326 | 9.5516 | 6700 | 4686 | NO | 29.2875 | 0 | 0 | 0 | 169.8675 | 1019.205 | DE14 | A
DE | DE148 | DEAG_BW4365100000057 | DETP_BW4365100000057 | SKA RIED | 47.7081 | 10.0058 | 40000 | 33469 | YES | 209.1813 | 669.38 | 502.035 | 1004.07 | 1213.2513 | 7279.5075 | DE14 | C
DE | DE149 | DEAG_BW4375100000007 | DETP_BW4375100000007 | SKA SIGMARINGENDORF | 48.066 | 9.2797 | 11900 | 10234 | NO | 63.9625 | 0 | 0 | 0 | 370.9825 | 2225.895 | DE14 | B
DE | DE149 | DEAG_BW4375100000008 | DETP_BW4375100000008 | SKA VERINGENDORF | 48.1522 | 9.1984 | 18300 | 5991 | NO | 37.4438 | 0 | 0 | 0 | 217.1738 | 1303.0425 | DE14 | B
DE | DE149 | DEAG_BW4375100000010 | DETP_BW4375100000010 | SKA STOV STETTEN | 48.1113 | 9.0657 | 8500 | 8112 | NO | 50.7 | 0 | 0 | 0 | 294.06 | 1764.36 | DE14 | C
DE | DE149 | DEAG_BW4375100000011 | DETP_BW4375100000011 | SKA SIGMARINGEN | 48.0771 | 9.2277 | 26000 | 24275 | NO | 151.7188 | 0 | 0 | 0 | 879.9687 | 5279.8125 | DE14 | A
DE | DE149 | DEAG_BW4375100000015 | DETP_BW4375100000015 | SKA BAD SAULGAU | 48.0272 | 9.4864 | 32000 | 19794 | NO | 123.7125 | 0 | 0 | 0 | 717.5325 | 4305.195 | DE14 | A
DE | DE149 | DEAG_BW4375100000017 | DETP_BW4375100000017 | SKA PFULLENDORF | 47.9332 | 9.2386 | 18000 | 15167 | NO | 94.7938 | 0 | 0 | 0 | 549.8037 | 3298.8225 | DE14 | A
DE | DE149 | DEAG_BW4375100000021 | DETP_BW4375100000021 | SKA MESSKIRCH | 48.0031 | 9.1683 | 17000 | 12071 | NO | 75.4438 | 0 | 0 | 0 | 437.5738 | 2625.4425 | DE14 | C
DE | DE149 | DEAG_BW4375100000023 | DETP_BW4375100000023 | SKA MENGEN | 48.0609 | 9.3428 | 26700 | 16121 | NO | 100.7563 | 0 | 0 | 0 | 584.3863 | 3506.3175 | DE14 | A
DE | DE149 | DEAG_BW4375100000027 | DETP_BW4375100000027 | SKA KRAUCHENWIES | 48.0274 | 9.2453 | 9500 | 6051 | NO | 37.8188 | 0 | 0 | 0 | 219.3487 | 1316.0925 | DE14 | C
DE | DE149 | DEAG_BW4375100000029 | DETP_BW4375100000029 | SKA HOHENTENGEN | 48.0509 | 9.3799 | 7000 | 3098 | NO | 19.3625 | 0 | 0 | 0 | 112.3025 | 673.815 | DE14 | B
DE | DE149 | DEAG_BW4375100000034 | DETP_BW4375100000034 | SKA HERBERTINGEN | 48.0678 | 9.4267 | 9200 | 7367 | NO | 46.0437 | 0 | 0 | 0 | 267.0537 | 1602.3225 | DE14 | B
DE | DE149 | DEAG_BW4375100000038 | DETP_BW4375100000038 | SKA GAMMERTINGEN | 48.2386 | 9.2237 | 13800 | 7273 | NO | 45.4563 | 0 | 0 | 0 | 263.6463 | 1581.8775 | DE14 | B
DE | DE149 | DEAG_BW4375100000041 | DETP_BW4375100000041 | SKA OSTRACH | 47.9979 | 9.3401 | 16400 | 16732 | NO | 104.575 | 0 | 0 | 0 | 606.535 | 3639.21 | DE14 | C
DE | DE261 | DEAG_BYAB-K0002 | DETP_BYAB-K0002 | Aschaffenburg | 49.9784 | 9.1106 | 200000 | 180600 | YES | 1128.75 | 3612 | 2709 | 5418 | 6546.75 | 39280.5 | DE26 | A
DE | DE264 | DEAG_BYAB-K0008 | DETP_BYAB-K0008 | Kleinostheim , AV Untermain | 50.0253 | 9.0351 | 48000 | 32640 | YES | 204 | 652.8 | 489.6 | 979.2 | 1183.2 | 7099.2 | DE26 | A
DE | DE264 | DEAG_BYAB-K0010 | DETP_BYAB-K0010 | AZV Main-Mömling-Elsava, KA Heimbuchenthal | 49.8792 | 9.2887 | 6000 | 3800 | NO | 23.75 | 0 | 0 | 0 | 137.75 | 826.5 | DE26 | B
DE | DE264 | DEAG_BYAB-K0012 | DETP_BYAB-K0012 | Zweckverband Abwasserbeseitigung Kahlgrund | 50.0934 | 9.1375 | 40000 | 37000 | YES | 231.25 | 740 | 555 | 1110 | 1341.25 | 8047.5 | DE26 | C
DE | DE264 | DEAG_BYAB-K0014 | DETP_BYAB-K0014 | Alzenau | 50.0852 | 9.0513 | 25000 | 30000 | NO | 187.5 | 0 | 0 | 0 | 1087.5 | 6525 | DE26 | A
DE | DE264 | DEAG_BYAB-K0016 | DETP_BYAB-K0016 | KA Bachgau | 49.9228 | 9.0909 | 35000 | 39000 | NO | 243.75 | 0 | 0 | 0 | 1413.75 | 8482.5 | DE26 | B
DE | DE264 | DEAG_BYAB-K0017 | DETP_BYAB-K0017 | Abwasserverband der Aschafftalgemeinden | 50.0015 | 9.2354 | 40000 | 26849 | YES | 167.8063 | 536.98 | 402.735 | 805.47 | 973.2763 | 5839.6575 | DE26 | A
DE | DE264 | DEAG_BYAB-K0018 | DETP_BYAB-K0018 | KA Kahl | 50.0644 | 8.9933 | 15000 | 8000 | NO | 50 | 0 | 0 | 0 | 290 | 1740 | DE26 | B
DE | DE269 | DEAG_BYAB-K0019 | DETP_BYAB-K0019 | Eichenbühl | 49.71 | 9.3192 | 8000 | 3200 | NO | 20 | 0 | 0 | 0 | 116 | 696 | DE26 | A
DE | DE269 | DEAG_BYAB-K0021 | DETP_BYAB-K0021 | KA AZV Südspessart | 49.7723 | 9.3897 | 16000 | 10100 | NO | 63.125 | 0 | 0 | 0 | 366.125 | 2196.75 | DE26 | A
DE | DE269 | DEAG_BYAB-K0022 | DETP_BYAB-K0022 | Elsenfeld, Gemeinschaftskläranlage Bayer. Untermain Gmbh | 49.8584 | 9.1607 | 185000 | 157654 | YES | 985.3375 | 3153.08 | 2364.81 | 4729.62 | 5714.9575 | 34289.745 | DE26 | A
DE | DE269 | DEAG_BYAB-K0026 | DETP_BYAB-K0026 | Abwasserzweckverband Main-Mud | 49.7114 | 9.2264 | 95000 | 67800 | YES | 423.75 | 1356 | 1017 | 2034 | 2457.75 | 14746.5 | DE26 | A
DE | DE269 | DEAG_BYAB-K0028 | DETP_BYAB-K0028 | Niedernberg | 49.9252 | 9.1389 | 7000 | 6500 | NO | 40.625 | 0 | 0 | 0 | 235.625 | 1413.75 | DE26 | B
DE | DE263 | DEAG_BYAB-K0033 | DETP_BYAB-K0033 | Würzburg | 49.7965 | 9.8943 | 360000 | 206665 | YES | 1291.6562 | 4133.3 | 3099.975 | 6199.95 | 7491.6062 | 44949.6375 | DE26 | A
DE | DE268 | DEAG_BYAB-K0040 | DETP_BYAB-K0040 | Wiesentheid | 49.7945 | 10.3334 | 10000 | 6355 | NO | 39.7188 | 0 | 0 | 0 | 230.3687 | 1382.2125 | DE26 | A
DE | DE268 | DEAG_BYAB-K0058 | DETP_BYAB-K0058 | ZV Schwarzacher Becken S.Schwarzach | 49.7976 | 10.2184 | 18000 | 15816 | NO | 98.85 | 0 | 0 | 0 | 573.33 | 3439.98 | DE26 | B
DE | DE268 | DEAG_BYAB-K0062 | DETP_BYAB-K0062 | Kitzingen | 49.7085 | 10.1409 | 85000 | 38238 | YES | 238.9875 | 764.76 | 573.57 | 1147.14 | 1386.1275 | 8316.765 | DE26 | B
DE | DE268 | DEAG_BYAB-K0068 | DETP_BYAB-K0068 | Geiselwind | 49.7655 | 10.537 | 9000 | 3000 | NO | 18.75 | 0 | 0 | 0 | 108.75 | 652.5 | DE26 | C
DE | DE268 | DEAG_BYAB-K0070 | DETP_BYAB-K0070 | Nordheim/Main | 49.8545 | 10.1752 | 10000 | 4820 | NO | 30.125 | 0 | 0 | 0 | 174.725 | 1048.35 | DE26 | B
DE | DE268 | DEAG_BYAB-K0071 | DETP_BYAB-K0071 | Volkach | 49.8619 | 10.2239 | 25000 | 11461 | NO | 71.6313 | 0 | 0 | 0 | 415.4613 | 2492.7675 | DE26 | A
DE | DE268 | DEAG_BYAB-K0074 | DETP_BYAB-K0074 | Prichsenstadt | 49.8312 | 10.3262 | 6000 | 3128 | NO | 19.55 | 0 | 0 | 0 | 113.39 | 680.34 | DE26 | B
DE | DE268 | DEAG_BYAB-K0077 | DETP_BYAB-K0077 | Iphofen | 49.703 | 10.2461 | 9600 | 2941 | NO | 18.3813 | 0 | 0 | 0 | 106.6112 | 639.6675 | DE26 | A
DE | DE26C | DEAG_BYAB-K0082 | DETP_BYAB-K0082 | Güntersleben | 49.8589 | 9.9067 | 6500 | 4593 | NO | 28.7063 | 0 | 0 | 0 | 166.4963 | 998.9775 | DE26 | B
DE | DE26C | DEAG_BYAB-K0094 | DETP_BYAB-K0094 | Aub | 49.5493 | 10.0513 | 6000 | 2786 | NOT KNOWN | 17.4125 | 0 | 0 | 0 | 100.9925 | 605.955 | DE26 | A
DE | DE26C | DEAG_BYAB-K0098 | DETP_BYAB-K0098 | Helmstadt | 49.7602 | 9.6534 | 5500 | 2529 | NO | 15.8063 | 0 | 0 | 0 | 91.6762 | 550.0575 | DE26 | C
DE | DE26C | DEAG_BYAB-K0102 | DETP_BYAB-K0102 | ZV Obere Pleichach Sitz Unterpleichfeld | 49.8638 | 10.0298 | 16000 | 14387 | NO | 89.9188 | 0 | 0 | 0 | 521.5287 | 3129.1725 | DE26 | B
DE | DE26C | DEAG_BYAB-K0105 | DETP_BYAB-K0105 | ZV Raum Ochsenfurt Sitz Ochsenfurt | 49.7162 | 10.0018 | 95000 | 58494 | YES | 365.5875 | 1169.88 | 877.41 | 1754.82 | 2120.4075 | 12722.445 | DE26 | B
DE | DE26C | DEAG_BYAB-K0112 | DETP_BYAB-K0112 | ZV Uettingen-Roßbrunn Sitz Uettingen | 49.7884 | 9.7074 | 8500 | 3729 | NO | 23.3063 | 0 | 0 | 0 | 135.1763 | 811.0575 | DE26 | C
DE | DE26C | DEAG_BYAB-K0113 | DETP_BYAB-K0113 | ZV Ahlbach-Gruppe Sitz Waldbüttelbrunn | 49.7786 | 9.8073 | 22000 | 15322 | NO | 95.7625 | 0 | 0 | 0 | 555.4225 | 3332.535 | DE26 | C
DE | DE26C | DEAG_BYAB-K0114 | DETP_BYAB-K0114 | ZV Maintal-Würzburg S.Veitshöchheim | 49.8426 | 9.8692 | 26000 | 13898 | NO | 86.8625 | 0 | 0 | 0 | 503.8025 | 3022.815 | DE26 | A
DE | DE26C | DEAG_BYAB-K0115 | DETP_BYAB-K0115 | ZV Taubertal | 49.517 | 9.9885 | 5950 | 2245 | NO | 14.0312 | 0 | 0 | 0 | 81.3812 | 488.2875 | DE26 | C
DE | DE26A | DEAG_BYAB-K0137 | DETP_BYAB-K0137 | Marktheidenfeld | 49.8331 | 9.5836 | 41000 | 14943 | YES | 93.3938 | 298.86 | 224.145 | 448.29 | 541.6838 | 3250.1025 | DE26 | C
DE | DE26A | DEAG_BYAB-K0155 | DETP_BYAB-K0155 | Triefenstein | 49.7873 | 9.597 | 7500 | 4875 | NO | 30.4688 | 0 | 0 | 0 | 176.7188 | 1060.3125 | DE26 | C
DE | DE26A | DEAG_BYAB-K0156 | DETP_BYAB-K0156 | Lohrtal | 50.0319 | 9.5304 | 17000 | 6000 | NO | 37.5 | 0 | 0 | 0 | 217.5 | 1305 | DE26 | B
DE | DE26A | DEAG_BYAB-K0157 | DETP_BYAB-K0157 | Karlstadt | 49.982 | 9.7659 | 19500 | 8200 | NO | 51.25 | 0 | 0 | 0 | 297.25 | 1783.5 | DE26 | A
DE | DE26A | DEAG_BYAB-K0159 | DETP_BYAB-K0159 | KA Aubachtal | 50.0249 | 9.4546 | 8000 | 5200 | NO | 32.5 | 0 | 0 | 0 | 188.5 | 1131 | DE26 | C
DE | DE26A | DEAG_BYAB-K0166 | DETP_BYAB-K0166 | ZV Zellinger Becken Sitz Zellingen | 49.9106 | 9.8055 | 28000 | 16313 | NO | 101.9563 | 0 | 0 | 0 | 591.3463 | 3548.0775 | DE26 | B
DE | DE26A | DEAG_BYAB-K0169 | DETP_BYAB-K0169 | Lohr/Main | 49.9811 | 9.5883 | 40000 | 19917 | YES | 124.4813 | 398.34 | 298.755 | 597.51 | 721.9912 | 4331.9475 | DE26 | B
DE | DE26A | DEAG_BYAB-K0170 | DETP_BYAB-K0170 | Kreuzwertheim | 49.7708 | 9.5109 | 12000 | 5000 | NO | 31.25 | 0 | 0 | 0 | 181.25 | 1087.5 | DE26 | A
DE | DE26A | DEAG_BYAB-K0171 | DETP_BYAB-K0171 | Arnstein Werntal | 49.9629 | 9.9087 | 13000 | 7000 | NO | 43.75 | 0 | 0 | 0 | 253.75 | 1522.5 | DE26 | C
DE | DE26A | DEAG_BYAB-K0173 | DETP_BYAB-K0173 | Gemünden Zentralkläranlage | 50.0446 | 9.7008 | 19000 | 12920 | NO | 80.75 | 0 | 0 | 0 | 468.35 | 2810.1 | DE26 | B
DE | DE251 | DEAG_BYAN-K0001 | DETP_BYAN-K0001 | Ansbach | 49.2893 | 10.6046 | 90000 | 65415 | YES | 408.8438 | 1308.3 | 981.225 | 1962.45 | 2371.2937 | 14227.7625 | DE25 | B
DE | DE256 | DEAG_BYAN-K0034 | DETP_BYAN-K0034 | Rothenburg/Tauber | 49.396 | 10.1665 | 38000 | 15294 | YES | 95.5875 | 305.88 | 229.41 | 458.82 | 554.4075 | 3326.445 | DE25 | C
DE | DE256 | DEAG_BYAN-K0046 | DETP_BYAN-K0046 | Wassertrüdingen | 49.0344 | 10.6036 | 22600 | 15368 | NO | 96.05 | 0 | 0 | 0 | 557.09 | 3342.54 | DE25 | B
DE | DE256 | DEAG_BYAN-K0054 | DETP_BYAN-K0054 | Heilsbronn | 49.3358 | 10.8179 | 11000 | 10527 | NO | 65.7938 | 0 | 0 | 0 | 381.6037 | 2289.6225 | DE25 | B
DE | DE256 | DEAG_BYAN-K0108 | DETP_BYAN-K0108 | Windsbach | 49.2349 | 10.8472 | 12500 | 17863 | NO | 111.6438 | 0 | 0 | 0 | 647.5338 | 3885.2025 | DE25 | C
DE | DE256 | DEAG_BYAN-K0154 | DETP_BYAN-K0154 | Leutershausen | 49.2903 | 10.4224 | 30000 | 9757 | NO | 60.9812 | 0 | 0 | 0 | 353.6912 | 2122.1475 | DE25 | B
DE | DE256 | DEAG_BYAN-K0176 | DETP_BYAN-K0176 | Burgoberbach | 49.2274 | 10.592 | 5900 | 4076 | NO | 25.475 | 0 | 0 | 0 | 147.755 | 886.53 | DE25 | B
DE | DE256 | DEAG_BYAN-K0192 | DETP_BYAN-K0192 | Herrieden | 49.2277 | 10.5044 | 13000 | 5920 | NO | 37 | 0 | 0 | 0 | 214.6 | 1287.6 | DE25 | A
DE | DE256 | DEAG_BYAN-K0202 | DETP_BYAN-K0202 | Neuendettelsau | 49.2758 | 10.7925 | 17500 | 9350 | NO | 58.4375 | 0 | 0 | 0 | 338.9375 | 2033.625 | DE25 | B
DE | DE256 | DEAG_BYAN-K0204 | DETP_BYAN-K0204 | Bechhofen | 49.1576 | 10.6171 | 9900 | 8356 | NO | 52.225 | 0 | 0 | 0 | 302.905 | 1817.43 | DE25 | C
DE | DE25A | DEAG_BYAN-K0224 | DETP_BYAN-K0224 | Emskirchen | 49.5533 | 10.7271 | 7500 | 4345 | NO | 27.1562 | 0 | 0 | 0 | 157.5062 | 945.0375 | DE25 | B
DE | DE25A | DEAG_BYAN-K0241 | DETP_BYAN-K0241 | Langenfeld | 49.6214 | 10.5208 | 9800 | 14062 | NO | 87.8875 | 0 | 0 | 0 | 509.7475 | 3058.485 | DE25 | B
DE | DE25A | DEAG_BYAN-K0284 | DETP_BYAN-K0284 | Uffenheim | 49.5496 | 10.2306 | 16000 | 6805 | NO | 42.5312 | 0 | 0 | 0 | 246.6813 | 1480.0875 | DE25 | A
DE | DE25A | DEAG_BYAN-K0312 | DETP_BYAN-K0312 | Bad Windsheim | 49.5053 | 10.4385 | 45000 | 28405 | YES | 177.5312 | 568.1 | 426.075 | 852.15 | 1029.6812 | 6178.0875 | DE25 | A
DE | DE25A | DEAG_BYAN-K0314 | DETP_BYAN-K0314 | Neustadt a.d.Aisch | 49.5855 | 10.6171 | 32500 | 23885 | NO | 149.2812 | 0 | 0 | 0 | 865.8312 | 5194.9875 | DE25 | A
DE | DE25A | DEAG_BYAN-K0321 | DETP_BYAN-K0321 | Scheinfeld | 49.6512 | 10.4719 | 8000 | 4954 | NO | 30.9625 | 0 | 0 | 0 | 179.5825 | 1077.495 | DE25 | C
DE | DE25C | DEAG_BYAN-K0335 | DETP_BYAN-K0335 | ZV Brombachsee Sitz Pleinfeld | 49.1248 | 10.9979 | 30000 | 14319 | NO | 89.4937 | 0 | 0 | 0 | 519.0637 | 3114.3825 | DE25 | C
DE | DE25C | DEAG_BYAN-K0348 | DETP_BYAN-K0348 | Pappenheim | 48.9227 | 10.9668 | 7200 | 4680 | NO | 29.25 | 0 | 0 | 0 | 169.65 | 1017.9 | DE25 | A
DE | DE25C | DEAG_BYAN-K0405 | DETP_BYAN-K0405 | Gunzenhausen | 49.104 | 10.7578 | 35000 | 33790 | NO | 211.1875 | 0 | 0 | 0 | 1224.8875 | 7349.325 | DE25 | A
DE | DE25C | DEAG_BYAN-K0416 | DETP_BYAN-K0416 | Weissenburg/Bay. | 49.0341 | 10.9619 | 35000 | 22295 | NO | 139.3438 | 0 | 0 | 0 | 808.1937 | 4849.1625 | DE25 | A
DE | DE25C | DEAG_BYAN-K0418 | DETP_BYAN-K0418 | Treuchtlingen | 48.9492 | 10.9113 | 45000 | 13706 | YES | 85.6625 | 274.12 | 205.59 | 411.18 | 496.8425 | 2981.055 | DE25 | B
DE | DE256 | DEAG_BYAN-K0430 | DETP_BYAN-K0430 | Dinkelsbühl | 49.0586 | 10.3339 | 29000 | 16454 | NO | 102.8375 | 0 | 0 | 0 | 596.4575 | 3578.745 | DE25 | A
DE | DE25A | DEAG_BYAN-K0452 | DETP_BYAN-K0452 | Burgbernheim | 49.469 | 10.3329 | 8000 | 6794 | NO | 42.4625 | 0 | 0 | 0 | 246.2825 | 1477.695 | DE25 | C
DE | DE256 | DEAG_BYAN-K0468 | DETP_BYAN-K0468 | Dietenhofen | 49.3963 | 10.7195 | 12000 | 7300 | NO | 45.625 | 0 | 0 | 0 | 264.625 | 1587.75 | DE25 | C
DE | DE256 | DEAG_BYAN-K0469 | DETP_BYAN-K0469 | Feuchtwangen | 49.1528 | 10.3382 | 19000 | 16334 | NO | 102.0875 | 0 | 0 | 0 | 592.1075 | 3552.645 | DE25 | B
DE | DE25A | DEAG_BYAN-K0470 | DETP_BYAN-K0470 | Gerhardshofen | 49.6349 | 10.6947 | 5000 | 3644 | NO | 22.775 | 0 | 0 | 0 | 132.095 | 792.57 | DE25 | B
DE | DE256 | DEAG_BYAN-K0472 | DETP_BYAN-K0472 | Lichtenau | 49.2774 | 10.6906 | 9500 | 3600 | NO | 22.5 | 0 | 0 | 0 | 130.5 | 783 | DE25 | A
DE | DE223 | DEAG_BYDEG-K0001 | DETP_BYDEG-K0001 | Straubing | 48.9009 | 12.6248 | 200000 | 68664 | YES | 429.15 | 1373.28 | 1029.96 | 2059.92 | 2489.07 | 14934.42 | DE22 | C
DE | DE224 | DEAG_BYDEG-K0008 | DETP_BYDEG-K0008 | Plattling | 48.7764 | 12.887 | 48000 | 16000 | YES | 100 | 320 | 240 | 480 | 580 | 3480 | DE22 | A
DE | DE224 | DEAG_BYDEG-K0012 | DETP_BYDEG-K0012 | Winzer | 48.7152 | 13.0893 | 22600 | 20271 | NO | 126.6938 | 0 | 0 | 0 | 734.8238 | 4408.9425 | DE22 | A
DE | DE224 | DEAG_BYDEG-K0013 | DETP_BYDEG-K0013 | Metten | 48.8464 | 12.9128 | 10000 | 6112 | NO | 38.2 | 0 | 0 | 0 | 221.56 | 1329.36 | DE22 | A
DE | DE224 | DEAG_BYDEG-K0014 | DETP_BYDEG-K0014 | Moos | 48.7587 | 12.9676 | 19990 | 16959 | NO | 105.9937 | 0 | 0 | 0 | 614.7637 | 3688.5825 | DE22 | B
DE | DE224 | DEAG_BYDEG-K0015 | DETP_BYDEG-K0015 | Schöllnach | 48.7481 | 13.1871 | 5250 | 4706 | NO | 29.4125 | 0 | 0 | 0 | 170.5925 | 1023.555 | DE22 | A
DE | DE224 | DEAG_BYDEG-K0018 | DETP_BYDEG-K0018 | ZV Hengersberg Sitz Hengersberg | 48.7578 | 13.0295 | 28000 | 19114 | NO | 119.4625 | 0 | 0 | 0 | 692.8825 | 4157.295 | DE22 | B
DE | DE224 | DEAG_BYDEG-K0030 | DETP_BYDEG-K0030 | Osterhofen | 48.7059 | 13.0366 | 14000 | 8100 | NO | 50.625 | 0 | 0 | 0 | 293.625 | 1761.75 | DE22 | B
DE | DE224 | DEAG_BYDEG-K0035 | DETP_BYDEG-K0035 | Deggendorf | 48.8117 | 12.9713 | 46000 | 39697 | YES | 248.1063 | 793.94 | 595.455 | 1190.91 | 1439.0162 | 8634.0975 | DE22 | A
DE | DE229 | DEAG_BYDEG-K0037 | DETP_BYDEG-K0037 | Regen | 48.9692 | 13.1051 | 18000 | 17055 | NO | 106.5938 | 0 | 0 | 0 | 618.2437 | 3709.4625 | DE22 | A
DE | DE229 | DEAG_BYDEG-K0045 | DETP_BYDEG-K0045 | Ruhmannsfelden | 48.9899 | 12.9899 | 9700 | 4796 | NO | 29.975 | 0 | 0 | 0 | 173.855 | 1043.13 | DE22 | A
DE | DE229 | DEAG_BYDEG-K0047 | DETP_BYDEG-K0047 | Bodenmais | 49.0627 | 13.0778 | 27000 | 13476 | NO | 84.225 | 0 | 0 | 0 | 488.505 | 2931.03 | DE22 | C
DE | DE229 | DEAG_BYDEG-K0050 | DETP_BYDEG-K0050 | Kirchberg | 48.9088 | 13.1981 | 6500 | 3648 | NO | 22.8 | 0 | 0 | 0 | 132.24 | 793.44 | DE22 | C
DE | DE229 | DEAG_BYDEG-K0051 | DETP_BYDEG-K0051 | ZV Zellertal Sitz Arnbruck | 49.0993 | 13.0037 | 9500 | 6515 | NO | 40.7188 | 0 | 0 | 0 | 236.1687 | 1417.0125 | DE22 | C
DE | DE229 | DEAG_BYDEG-K0062 | DETP_BYDEG-K0062 | Viechtach | 49.0834 | 12.8888 | 30000 | 22358 | NO | 139.7375 | 0 | 0 | 0 | 810.4775 | 4862.865 | DE22 | A
DE | DE229 | DEAG_BYDEG-K0065 | DETP_BYDEG-K0065 | Teisnach | 49.0427 | 12.9945 | 21000 | 14526 | NO | 90.7875 | 0 | 0 | 0 | 526.5675 | 3159.405 | DE22 | A
DE | DE229 | DEAG_BYDEG-K0066 | DETP_BYDEG-K0066 | Zwiesel | 49.007 | 13.1995 | 28700 | 20183 | NO | 126.1438 | 0 | 0 | 0 | 731.6337 | 4389.8025 | DE22 | C
DE | DE229 | DEAG_BYDEG-K0067 | DETP_BYDEG-K0067 | Bischofsmais-Langbruck | 48.9262 | 13.1154 | 8500 | 4583 | NO | 28.6438 | 0 | 0 | 0 | 166.1337 | 996.8025 | DE22 | C
DE | DE22B | DEAG_BYDEG-K0074 | DETP_BYDEG-K0074 | Bogen | 48.895 | 12.7126 | 15000 | 11396 | NO | 71.225 | 0 | 0 | 0 | 413.105 | 2478.63 | DE22 | A
DE | DE22B | DEAG_BYDEG-K0079 | DETP_BYDEG-K0079 | Mallersdorf-Pfaffenberg | 48.7754 | 12.2695 | 10000 | 7951 | NO | 49.6938 | 0 | 0 | 0 | 288.2237 | 1729.3425 | DE22 | B
DE | DE22B | DEAG_BYDEG-K0083 | DETP_BYDEG-K0083 | Niederwinkling | 48.8816 | 12.8032 | 5166 | 2981 | NO | 18.6313 | 0 | 0 | 0 | 108.0613 | 648.3675 | DE22 | B
DE | DE22B | DEAG_BYDEG-K0086 | DETP_BYDEG-K0086 | Hunderdorf | 48.9371 | 12.7349 | 5500 | 4400 | NO | 27.5 | 0 | 0 | 0 | 159.5 | 957 | DE22 | B
DE | DE22B | DEAG_BYDEG-K0101 | DETP_BYDEG-K0101 | Geiselhöring | 48.8371 | 12.4078 | 12000 | 9117 | NO | 56.9812 | 0 | 0 | 0 | 330.4912 | 1982.9475 | DE22 | C
DE | DE22B | DEAG_BYDEG-K0105 | DETP_BYDEG-K0105 | Straßkirchen | 48.8369 | 12.7675 | 11900 | 9250 | NO | 57.8125 | 0 | 0 | 0 | 335.3125 | 2011.875 | DE22 | B
DE | DE22B | DEAG_BYDEG-K0115 | DETP_BYDEG-K0115 | Parkstetten | 48.9112 | 12.6329 | 5500 | 3340 | NO | 20.875 | 0 | 0 | 0 | 121.075 | 726.45 | DE22 | C
DE | DE22B | DEAG_BYDEG-K0129 | DETP_BYDEG-K0129 | Sankt Englmar | 48.9945 | 12.8287 | 5000 | 3217 | NO | 20.1062 | 0 | 0 | 0 | 116.6162 | 699.6975 | DE22 | B
DE | DE222 | DEAG_BYDEG-K0142 | DETP_BYDEG-K0142 | Passau-Haibach | 48.5749 | 13.4984 | 110000 | 88500 | YES | 553.125 | 1770 | 1327.5 | 2655 | 3208.125 | 19248.75 | DE22 | A
DE | DE228 | DEAG_BYDEG-K0149 | DETP_BYDEG-K0149 | Büchlberg | 48.6775 | 13.5242 | 5000 | 4629 | NO | 28.9313 | 0 | 0 | 0 | 167.8013 | 1006.8075 | DE22 | B
DE | DE228 | DEAG_BYDEG-K0151 | DETP_BYDEG-K0151 | Wegscheid | 48.5928 | 13.7982 | 6000 | 3803 | NO | 23.7688 | 0 | 0 | 0 | 137.8587 | 827.1525 | DE22 | B
DE | DE228 | DEAG_BYDEG-K0154 | DETP_BYDEG-K0154 | Hauzenberg-Aubachtal | 48.6121 | 13.6388 | 6000 | 3156 | NO | 19.725 | 0 | 0 | 0 | 114.405 | 686.43 | DE22 | C
DE | DE228 | DEAG_BYDEG-K0155 | DETP_BYDEG-K0155 | Eging am See | 48.7224 | 13.2637 | 7000 | 3517 | NO | 21.9812 | 0 | 0 | 0 | 127.4912 | 764.9475 | DE22 | B
DE | DE228 | DEAG_BYDEG-K0174 | DETP_BYDEG-K0174 | Thyrnau | 48.5856 | 13.533 | 6500 | 10514 | NO | 65.7125 | 0 | 0 | 0 | 381.1325 | 2286.795 | DE22 | C
DE | DE228 | DEAG_BYDEG-K0175 | DETP_BYDEG-K0175 | Aldersbach | 48.2991 | 11.2741 | 20000 | 7164 | NO | 44.775 | 0 | 0 | 0 | 259.695 | 1558.17 | DE21 | C
DE | DE228 | DEAG_BYDEG-K0178 | DETP_BYDEG-K0178 | Ruhstorf an der Rott | 48.4494 | 13.375 | 14200 | 14368 | NO | 89.8 | 0 | 0 | 0 | 520.84 | 3125.04 | DE22 | C
DE | DE228 | DEAG_BYDEG-K0183 | DETP_BYDEG-K0183 | Bad Griesbach im Rottal | 48.4133 | 13.222 | 27000 | 11348 | NO | 70.925 | 0 | 0 | 0 | 411.365 | 2468.19 | DE22 | C
DE | DE228 | DEAG_BYDEG-K0189 | DETP_BYDEG-K0189 | Hutthurm | 48.687 | 13.4505 | 21000 | 19175 | NO | 119.8438 | 0 | 0 | 0 | 695.0937 | 4170.5625 | DE22 | A
DE | DE228 | DEAG_BYDEG-K0191 | DETP_BYDEG-K0191 | Ortenburg-Blindham | 48.576 | 13.2028 | 11000 | 7835 | NO | 48.9688 | 0 | 0 | 0 | 284.0187 | 1704.1125 | DE22 | B
DE | DE228 | DEAG_BYDEG-K0195 | DETP_BYDEG-K0195 | Vilshofen-Zentrum | 48.6275 | 13.2023 | 56000 | 66064 | YES | 412.9 | 1321.28 | 990.96 | 1981.92 | 2394.82 | 14368.92 | DE22 | A
DE | DE228 | DEAG_BYDEG-K0203 | DETP_BYDEG-K0203 | Pocking | 48.419 | 13.3375 | 17000 | 8524 | NO | 53.275 | 0 | 0 | 0 | 308.995 | 1853.97 | DE22 | B
DE | DE228 | DEAG_BYDEG-K0204 | DETP_BYDEG-K0204 | Bad Füssing | 48.3434 | 13.3414 | 95000 | 33946 | YES | 212.1625 | 678.92 | 509.19 | 1018.38 | 1230.5425 | 7383.255 | DE22 | C
DE | DE228 | DEAG_BYDEG-K0213 | DETP_BYDEG-K0213 | Hauzenberg-Kaindlmühle | 48.6111 | 13.5828 | 18000 | 13333 | NO | 83.3312 | 0 | 0 | 0 | 483.3212 | 2899.9275 | DE22 | C
DE | DE228 | DEAG_BYDEG-K0214 | DETP_BYDEG-K0214 | Tiefenbach | 48.6197 | 13.389 | 8000 | 4870 | NO | 30.4375 | 0 | 0 | 0 | 176.5375 | 1059.225 | DE22 | B
DE | DE228 | DEAG_BYDEG-K0217 | DETP_BYDEG-K0217 | Tittling | 48.7509 | 13.3946 | 12000 | 12700 | NO | 79.375 | 0 | 0 | 0 | 460.375 | 2762.25 | DE22 | C
DE | DE228 | DEAG_BYDEG-K0224 | DETP_BYDEG-K0224 | Salzweg | 48.6056 | 13.478 | 6000 | 4411 | NO | 27.5687 | 0 | 0 | 0 | 159.8987 | 959.3925 | DE22 | A
DE | DE228 | DEAG_BYDEG-K0226 | DETP_BYDEG-K0226 | Ruderting | 48.6503 | 13.44 | 5000 | 2683 | NO | 16.7688 | 0 | 0 | 0 | 97.2588 | 583.5525 | DE22 | C
DE | DE228 | DEAG_BYDEG-K0228 | DETP_BYDEG-K0228 | Obernzell | 48.5621 | 13.6164 | 7500 | 2525 | NO | 15.7812 | 0 | 0 | 0 | 91.5312 | 549.1875 | DE22 | C
DE | DE225 | DEAG_BYDEG-K0231 | DETP_BYDEG-K0231 | Freyung | 48.8098 | 13.5375 | 17000 | 11700 | NO | 73.125 | 0 | 0 | 0 | 424.125 | 2544.75 | DE22 | A
DE | DE225 | DEAG_BYDEG-K0236 | DETP_BYDEG-K0236 | Grafenau | 48.8575 | 13.3859 | 9900 | 6160 | NO | 38.5 | 0 | 0 | 0 | 223.3 | 1339.8 | DE22 | A
DE | DE225 | DEAG_BYDEG-K0237 | DETP_BYDEG-K0237 | Spiegelau | 48.9111 | 13.3588 | 7500 | 4550 | NO | 28.4375 | 0 | 0 | 0 | 164.9375 | 989.625 | DE22 | A
DE | DE225 | DEAG_BYDEG-K0238 | DETP_BYDEG-K0238 | Spiegelau OT Augrub | 48.8794 | 13.3347 | 6500 | 3106 | NO | 19.4125 | 0 | 0 | 0 | 112.5925 | 675.555 | DE22 | C
DE | DE225 | DEAG_BYDEG-K0248 | DETP_BYDEG-K0248 | Neureichenau | 48.7419 | 13.7509 | 6000 | 3833 | NO | 23.9563 | 0 | 0 | 0 | 138.9462 | 833.6775 | DE22 | A
DE | DE225 | DEAG_BYDEG-K0251 | DETP_BYDEG-K0251 | ZV Neuschönau-Sankt Oswald | 48.8669 | 13.452 | 6000 | 4206 | NO | 26.2875 | 0 | 0 | 0 | 152.4675 | 914.805 | DE22 | B
DE | DE225 | DEAG_BYDEG-K0252 | DETP_BYDEG-K0252 | Röhrnbach | 48.7302 | 13.5244 | 8000 | 6363 | NO | 39.7688 | 0 | 0 | 0 | 230.6588 | 1383.9525 | DE22 | B
DE | DE225 | DEAG_BYDEG-K0262 | DETP_BYDEG-K0262 | Schönberg | 48.8224 | 13.3527 | 8800 | 5035 | NOT KNOWN | 31.4688 | 0 | 0 | 0 | 182.5187 | 1095.1125 | DE22 | C
DE | DE225 | DEAG_BYDEG-K0292 | DETP_BYDEG-K0292 | Grafenau OT Furth | 48.7888 | 13.3904 | 6500 | 2218 | NO | 13.8625 | 0 | 0 | 0 | 80.4025 | 482.415 | DE22 | C
DE | DE225 | DEAG_BYDEG-K0301 | DETP_BYDEG-K0301 | Waldkirchen | 48.7267 | 13.5523 | 16000 | 10662 | NO | 66.6375 | 0 | 0 | 0 | 386.4975 | 2318.985 | DE22 | C
DE | DE22A | DEAG_BYDEG-K0307 | DETP_BYDEG-K0307 | Gangkofen | 48.4325 | 12.572 | 7900 | 7367 | NO | 46.0437 | 0 | 0 | 0 | 267.0537 | 1602.3225 | DE22 | A
DE | DE22A | DEAG_BYDEG-K0311 | DETP_BYDEG-K0311 | Arnstorf | 48.5676 | 12.8202 | 20000 | 6980 | NO | 43.625 | 0 | 0 | 0 | 253.025 | 1518.15 | DE22 | A
DE | DE22A | DEAG_BYDEG-K0320 | DETP_BYDEG-K0320 | Tann | 48.3093 | 12.8959 | 12000 | 3050 | NO | 19.0625 | 0 | 0 | 0 | 110.5625 | 663.375 | DE22 | A
DE | DE22A | DEAG_BYDEG-K0346 | DETP_BYDEG-K0346 | Eggenfelden | 48.404 | 12.7779 | 91930 | 39450 | NO | 246.5625 | 0 | 0 | 0 | 1430.0625 | 8580.375 | DE22 | A
DE | DE22A | DEAG_BYDEG-K0347 | DETP_BYDEG-K0347 | Simbach am Inn | 48.2667 | 13.0367 | 19500 | 16150 | NO | 100.9375 | 0 | 0 | 0 | 585.4375 | 3512.625 | DE22 | A
DE | DE22A | DEAG_BYDEG-K0355 | DETP_BYDEG-K0355 | Massing | 48.3931 | 12.6231 | 6000 | 7645 | NO | 47.7812 | 0 | 0 | 0 | 277.1312 | 1662.7875 | DE22 | B
DE | DE22A | DEAG_BYDEG-K0364 | DETP_BYDEG-K0364 | Bad Birnbach | 48.4331 | 13.1005 | 12500 | 17468 | NO | 109.175 | 0 | 0 | 0 | 633.215 | 3799.29 | DE22 | B
DE | DE22A | DEAG_BYDEG-K0366 | DETP_BYDEG-K0366 | Roßbach | 48.6013 | 12.9395 | 30000 | 11626 | NO | 72.6625 | 0 | 0 | 0 | 421.4425 | 2528.655 | DE22 | B
DE | DE22A | DEAG_BYDEG-K0369 | DETP_BYDEG-K0369 | Pfarrkirchen | 48.4314 | 12.9648 | 49500 | 22026 | YES | 137.6625 | 440.52 | 330.39 | 660.78 | 798.4425 | 4790.655 | DE22 | B
DE | DE271 | DEAG_BYDON-K0001 | DETP_BYDON-K0001 | Augsburg | 48.4126 | 10.8873 | 600000 | 500997 | YES | 3131.2313 | 10019.94 | 7514.955 | 15029.91 | 18161.1413 | 108966.8475 | DE27 | A
DE | DE276 | DEAG_BYDON-K0003 | DETP_BYDON-K0003 | Schwabmünchen | 48.2017 | 10.7286 | 25000 | 23850 | NO | 149.0625 | 0 | 0 | 0 | 864.5625 | 5187.375 | DE27 | C
DE | DE276 | DEAG_BYDON-K0006 | DETP_BYDON-K0006 | Zusmarshausen | 48.4246 | 10.5933 | 9000 | 9071 | NO | 56.6938 | 0 | 0 | 0 | 328.8237 | 1972.9425 | DE27 | C
DE | DE276 | DEAG_BYDON-K0011 | DETP_BYDON-K0011 | Langweid/Lech | 48.5004 | 10.865 | 15600 | 12197 | NO | 76.2313 | 0 | 0 | 0 | 442.1412 | 2652.8475 | DE27 | A
DE | DE276 | DEAG_BYDON-K0013 | DETP_BYDON-K0013 | Gersthofen | 48.4593 | 10.8803 | 31670 | 38765 | NO | 242.2812 | 0 | 0 | 0 | 1405.2312 | 8431.3875 | DE27 | C
DE | DE276 | DEAG_BYDON-K0014 | DETP_BYDON-K0014 | Dinkelscherben | 48.357 | 10.5703 | 12000 | 10850 | NO | 67.8125 | 0 | 0 | 0 | 393.3125 | 2359.875 | DE27 | B
DE | DE276 | DEAG_BYDON-K0016 | DETP_BYDON-K0016 | Fischach | 48.2938 | 10.6578 | 14000 | 11632 | NO | 72.7 | 0 | 0 | 0 | 421.66 | 2529.96 | DE27 | A
DE | DE276 | DEAG_BYDON-K0022 | DETP_BYDON-K0022 | Gablingen | 48.4597 | 10.8324 | 12000 | 7249 | NO | 45.3062 | 0 | 0 | 0 | 262.7762 | 1576.6575 | DE27 | B
DE | DE276 | DEAG_BYDON-K0023 | DETP_BYDON-K0023 | Ustersbach | 48.3176 | 10.6354 | 12000 | 8558 | NO | 53.4875 | 0 | 0 | 0 | 310.2275 | 1861.365 | DE27 | B
DE | DE276 | DEAG_BYDON-K0024 | DETP_BYDON-K0024 | Thierhaupten | 48.5745 | 10.8988 | 5000 | 3051 | NO | 19.0688 | 0 | 0 | 0 | 110.5987 | 663.5925 | DE27 | B
DE | DE146 | DEAG_BW4265100000002 | DETP_BW4265100000002 | SKA EROLZHEIM | 48.0996 | 10.0795 | 10500 | 13637 | NO | 85.2313 | 0 | 0 | 0 | 494.3413 | 2966.0475 | DE14 | B
DE | DE146 | DEAG_BW4265100000003 | DETP_BW4265100000003 | SKA RIEDLINGEN | 48.1655 | 9.4938 | 60000 | 44624 | YES | 278.9 | 892.48 | 669.36 | 1338.72 | 1617.62 | 9705.72 | DE14 | C
DE | DE146 | DEAG_BW4265100000004 | DETP_BW4265100000004 | SKA BALTRINGEN | 48.1804 | 9.8611 | 6000 | 8945 | NO | 55.9062 | 0 | 0 | 0 | 324.2562 | 1945.5375 | DE14 | B
DE | DE276 | DEAG_BYDON-K0025 | DETP_BYDON-K0025 | Bobingen | 48.2869 | 10.8289 | 28000 | 21242 | NO | 132.7625 | 0 | 0 | 0 | 770.0225 | 4620.135 | DE27 | C
DE | DE276 | DEAG_BYDON-K0029 | DETP_BYDON-K0029 | Meitingen | 48.5806 | 10.8663 | 16000 | 14280 | NO | 89.25 | 0 | 0 | 0 | 517.65 | 3105.9 | DE27 | C
DE | DE276 | DEAG_BYDON-K0031 | DETP_BYDON-K0031 | Wehringen | 48.258 | 10.7955 | 9000 | 5815 | NO | 36.3438 | 0 | 0 | 0 | 210.7937 | 1264.7625 | DE27 | B
DE | DE276 | DEAG_BYDON-K0035 | DETP_BYDON-K0035 | Welden | 48.4684 | 10.6537 | 6000 | 3530 | NO | 22.0625 | 0 | 0 | 0 | 127.9625 | 767.775 | DE27 | C
DE | DE276 | DEAG_BYDON-K0036 | DETP_BYDON-K0036 | AZV Donnsberggruppe Sitz Allmannshofen | 48.6173 | 10.8165 | 7500 | 7087 | NO | 44.2937 | 0 | 0 | 0 | 256.9037 | 1541.4225 | DE27 | B
DE | DE276 | DEAG_BYDON-K0039 | DETP_BYDON-K0039 | AZV Lechfeld | 48.2189 | 10.895 | 48000 | 32244 | YES | 201.525 | 644.88 | 483.66 | 967.32 | 1168.845 | 7013.07 | DE27 | A
DE | DE146 | DEAG_BW4265100000007 | DETP_BW4265100000007 | SKA WARTHAUSEN | 48.1433 | 9.796 | 99000 | 88305 | YES | 551.9062 | 1766.1 | 1324.575 | 2649.15 | 3201.0562 | 19206.3375 | DE14 | C
DE | DE146 | DEAG_BW4265100000008 | DETP_BW4265100000008 | SKA SCHEMMERBERG | 48.1999 | 9.8322 | 13200 | 10186 | NO | 63.6625 | 0 | 0 | 0 | 369.2425 | 2215.455 | DE14 | C
DE | DE146 | DEAG_BW4265100000009 | DETP_BW4265100000009 | SKA BAD BUCHAU | 48.065 | 9.5808 | 15000 | 11674 | NO | 72.9625 | 0 | 0 | 0 | 423.1825 | 2539.095 | DE14 | C
DE | DE146 | DEAG_BW4265100000010 | DETP_BW4265100000010 | SKA STETTEN | 48.2853 | 9.8968 | 5200 | 6993 | NO | 43.7063 | 0 | 0 | 0 | 253.4963 | 1520.9775 | DE14 | B
DE | DE146 | DEAG_BW4265100000011 | DETP_BW4265100000011 | SKA BAD SCHUSSENRIED | 47.9802 | 9.6569 | 16500 | 13144 | NO | 82.15 | 0 | 0 | 0 | 476.47 | 2858.82 | DE14 | C
DE | DE146 | DEAG_BW4265100000015 | DETP_BW4265100000015 | SKA EBERHARDZELL | 48.0083 | 9.8272 | 6000 | 6496 | NO | 40.6 | 0 | 0 | 0 | 235.48 | 1412.88 | DE14 | B
DE | DE146 | DEAG_BW4265100000023 | DETP_BW4265100000023 | SKA LAUPHEIM | 48.2505 | 9.8722 | 50000 | 30166 | YES | 188.5375 | 603.32 | 452.49 | 904.98 | 1093.5175 | 6561.105 | DE14 | B
DE | DE146 | DEAG_BW4265100000025 | DETP_BW4265100000025 | SKA ROT A.D. ROT | 48.0343 | 10.0452 | 5500 | 8771 | NO | 54.8188 | 0 | 0 | 0 | 317.9487 | 1907.6925 | DE14 | C
DE | DE146 | DEAG_BW4265100000030 | DETP_BW4265100000030 | SKA SCHÖNEBÜRG | 48.1651 | 9.9302 | 14800 | 16363 | NO | 102.2688 | 0 | 0 | 0 | 593.1588 | 3558.9525 | DE14 | C
DE | DE146 | DEAG_BW4265100000035 | DETP_BW4265100000035 | SKA BURGRIEDEN | 48.2434 | 9.9201 | 14800 | 15815 | NO | 98.8438 | 0 | 0 | 0 | 573.2938 | 3439.7625 | DE14 | B
DE | DE147 | DEAG_BW4355100000004 | DETP_BW4355100000004 | SKA APFLAU | 47.6304 | 9.6135 | 9375 | 4885 | NO | 30.5312 | 0 | 0 | 0 | 177.0812 | 1062.4875 | DE14 | C
DE | DE147 | DEAG_BW4355100000005 | DETP_BW4355100000005 | SKA FRICKINGEN | 47.8049 | 9.269 | 13600 | 14827 | NO | 92.6688 | 0 | 0 | 0 | 537.4787 | 3224.8725 | DE14 | B
DE | DE147 | DEAG_BW4355100000006 | DETP_BW4355100000006 | SKA Grasbeuren | 47.7275 | 9.2999 | 13800 | 6198 | NO | 38.7375 | 0 | 0 | 0 | 224.6775 | 1348.065 | DE14 | C
DE | DE147 | DEAG_BW4355100000007 | DETP_BW4355100000007 | SKA UHLDINGEN | 47.7308 | 9.234 | 66000 | 71661 | NO | 447.8812 | 0 | 0 | 0 | 2597.7112 | 15586.2675 | DE14 | B
DE | DE147 | DEAG_BW4355100000008 | DETP_BW4355100000008 | SKA BUGGENSEGEL | 47.7456 | 9.3137 | 15000 | 16745 | NO | 104.6562 | 0 | 0 | 0 | 607.0062 | 3642.0375 | DE14 | C
DE | DE147 | DEAG_BW4355100000009 | DETP_BW4355100000009 | SKA KRESSBRONN | 47.5948 | 9.5814 | 24000 | 23398 | NO | 146.2375 | 0 | 0 | 0 | 848.1775 | 5089.065 | DE14 | B
DE | DE147 | DEAG_BW4355100000010 | DETP_BW4355100000010 | SKA Immenstaad | 47.6715 | 9.3887 | 40000 | 30403 | NO | 190.0187 | 0 | 0 | 0 | 1102.1087 | 6612.6525 | DE14 | A
DE | DE147 | DEAG_BW4355100000011 | DETP_BW4355100000011 | SKA ERISKIRCH | 47.619 | 9.5323 | 50000 | 53100 | YES | 331.875 | 1062 | 796.5 | 1593 | 1924.875 | 11549.25 | DE14 | A
DE | DE275 | DEAG_BYDON-K0144 | DETP_BYDON-K0144 | Pöttmes | 48.5813 | 11.1116 | 12000 | 6151 | NO | 38.4438 | 0 | 0 | 0 | 222.9737 | 1337.8425 | DE27 | B
DE | DE275 | DEAG_BYDON-K0146 | DETP_BYDON-K0146 | AZV Kabisbachgruppe | 48.5212 | 10.9035 | 18500 | 20276 | NO | 126.725 | 0 | 0 | 0 | 735.005 | 4410.03 | DE27 | C
DE | DE275 | DEAG_BYDON-K0155 | DETP_BYDON-K0155 | Dasing | 48.3947 | 11.0587 | 8550 | 7103 | NO | 44.3938 | 0 | 0 | 0 | 257.4837 | 1544.9025 | DE27 | B
DE | DE275 | DEAG_BYDON-K0158 | DETP_BYDON-K0158 | Affing | 48.4623 | 10.9355 | 8500 | 4466 | NO | 27.9125 | 0 | 0 | 0 | 161.8925 | 971.355 | DE27 | B
DE | DE275 | DEAG_BYDON-K0162 | DETP_BYDON-K0162 | Friedberg-Paar | 48.3698 | 11.0403 | 16800 | 9270 | NO | 57.9375 | 0 | 0 | 0 | 336.0375 | 2016.225 | DE27 | B
DE | DE277 |  | DETP_BYDON-K0181 | ZV Untere Brenz Sitz Bächingen | 48.5433 | 10.3307 | 9900 | 7746 | NO | 48.4125 | 0 | 0 | 0 | 280.7925 | 1684.755 | DE27 | C
DE | DE277 | DEAG_BYDON-K0185 | DETP_BYDON-K0185 | Bissingen | 48.7096 | 10.6282 | 35000 | 28081 | NO | 175.5062 | 0 | 0 | 0 | 1017.9362 | 6107.6175 | DE27 | B
DE | DE277 | DEAG_BYDON-K0186 | DETP_BYDON-K0186 | Lauingen | 48.5688 | 10.4508 | 28500 | 13408 | YES | 83.8 | 268.16 | 201.12 | 402.24 | 486.04 | 2916.24 | DE27 | A
DE | DE277 | DEAG_BYDON-K0189 | DETP_BYDON-K0189 | Gundelfingen | 48.5511 | 10.388 | 25000 | 12018 | NO | 75.1125 | 0 | 0 | 0 | 435.6525 | 2613.915 | DE27 | B
DE | DE277 | DEAG_BYDON-K0190 | DETP_BYDON-K0190 | Wertingen | 48.5706 | 10.7004 | 15000 | 11950 | NO | 74.6875 | 0 | 0 | 0 | 433.1875 | 2599.125 | DE27 | C
DE | DE277 | DEAG_BYDON-K0191 | DETP_BYDON-K0191 | Dillingen / Donau | 48.5715 | 10.5107 | 45000 | 28698 | YES | 179.3625 | 573.96 | 430.47 | 860.94 | 1040.3025 | 6241.815 | DE27 | A
DE | DE277 | DEAG_BYDON-K0192 | DETP_BYDON-K0192 | Höchstädt / Donau | 48.6155 | 10.5826 | 8300 | 5562 | NO | 34.7625 | 0 | 0 | 0 | 201.6225 | 1209.735 | DE27 | B
DE | DE277 | DEAG_BYDON-K0193 | DETP_BYDON-K0193 | Syrgenstein-Vg | 48.6264 | 10.3318 | 8000 | 5276 | NO | 32.975 | 0 | 0 | 0 | 191.255 | 1147.53 | DE27 | C
DE | DE277 | DEAG_BYDON-K0196 | DETP_BYDON-K0196 | Buttenwiesen OT Lauterbach | 48.6307 | 10.743 | 10000 | 6044 | NO | 37.775 | 0 | 0 | 0 | 219.095 | 1314.57 | DE27 | B
DE | DE278 | DEAG_BYDON-K0198 | DETP_BYDON-K0198 | Burgau | 48.4403 | 10.4061 | 18750 | 11117 | NO | 69.4813 | 0 | 0 | 0 | 402.9912 | 2417.9475 | DE27 | A
DE | DE278 | DEAG_BYDON-K0199 | DETP_BYDON-K0199 | Leipheim | 48.4546 | 10.229 | 16000 | 13511 | NO | 84.4438 | 0 | 0 | 0 | 489.7738 | 2938.6425 | DE27 | B
DE | DE278 | DEAG_BYDON-K0201 | DETP_BYDON-K0201 | Krumbach | 48.2776 | 10.3555 | 30000 | 32167 | NO | 201.0438 | 0 | 0 | 0 | 1166.0538 | 6996.3225 | DE27 | B
DE | DE278 | DEAG_BYDON-K0205 | DETP_BYDON-K0205 | ZV Mindel-Gruppe Sitz Thannhausen | 48.2929 | 10.4615 | 35000 | 14368 | NO | 89.8 | 0 | 0 | 0 | 520.84 | 3125.04 | DE27 | A
DE | DE278 | DEAG_BYDON-K0208 | DETP_BYDON-K0208 | ZV Burtenbach-Münsterhausen S.Burtenba. | 48.346 | 10.4414 | 6000 | 3850 | NO | 24.0625 | 0 | 0 | 0 | 139.5625 | 837.375 | DE27 | B
DE | DE278 | DEAG_BYDON-K0209 | DETP_BYDON-K0209 | Jettingen-Scheppach | 48.4102 | 10.4261 | 18000 | 11850 | NO | 74.0625 | 0 | 0 | 0 | 429.5625 | 2577.375 | DE27 | B
DE | DE278 | DEAG_BYDON-K0210 | DETP_BYDON-K0210 | Ziemetshausen | 48.2985 | 10.5414 | 6350 | 4668 | NO | 29.175 | 0 | 0 | 0 | 169.215 | 1015.29 | DE27 | B
DE | DE278 | DEAG_BYDON-K0211 | DETP_BYDON-K0211 | Günzburg | 48.4643 | 10.2886 | 110000 | 66574 | YES | 416.0875 | 1331.48 | 998.61 | 1997.22 | 2413.3075 | 14479.845 | DE27 | A
DE | DE278 | DEAG_BYDON-K0212 | DETP_BYDON-K0212 | Bibertal | 48.4238 | 10.1852 | 5000 | 3657 | NO | 22.8563 | 0 | 0 | 0 | 132.5663 | 795.3975 | DE27 | B
DE | DE278 | DEAG_BYDON-K0213 | DETP_BYDON-K0213 | ZV Unteres Günztal Sitz Ichenhausen | 48.4162 | 10.2788 | 27500 | 24261 | NO | 151.6312 | 0 | 0 | 0 | 879.4612 | 5276.7675 | DE27 | B
DE | DE278 | DEAG_BYDON-K0215 | DETP_BYDON-K0215 | ZV Mindel-Kammel Sitz Offingen | 48.4894 | 10.3828 | 30000 | 29300 | NO | 183.125 | 0 | 0 | 0 | 1062.125 | 6372.75 | DE27 | A
DE | DE279 |  | DETP_BYDON-K0216 | Vöhringen | 48.2874 | 10.0669 | 40000 | 25652 | YES | 160.325 | 513.04 | 384.78 | 769.56 | 929.885 | 5579.31 | DE27 | A
DE | DE279 | DEAG_BYDON-K0218 | DETP_BYDON-K0218 | ZV Mittleres Rothtal S. Pfaffenhofen | 48.3608 | 10.1575 | 11000 | 5421 | NO | 33.8813 | 0 | 0 | 0 | 196.5113 | 1179.0675 | DE27 | A
DE | DE279 |  | DETP_BYDON-K0220 | Zweckverband Klärwerk Steinhäule | 48.4245 | 10.0313 | 445000 | 413317 | YES | 2583.2313 | 8266.34 | 6199.755 | 12399.51 | 14982.7413 | 89896.4475 | DE14 | A
DE | DE279 | DEAG_BYDON-K0222 | DETP_BYDON-K0222 | Nersingen | 48.4362 | 10.1247 | 15000 | 4806 | NO | 30.0375 | 0 | 0 | 0 | 174.2175 | 1045.305 | DE27 | A
DE | DE279 |  | DETP_BYDON-K0227 | ZV Mittleres Illertal Sitz Illertissen | 48.2505 | 10.0756 | 95000 | 43400 | YES | 271.25 | 868 | 651 | 1302 | 1573.25 | 9439.5 | DE27 | B
DE | DE279 | DEAG_BYDON-K0232 | DETP_BYDON-K0232 | Elchingen | 48.445 | 10.0938 | 22000 | 9533 | NO | 59.5813 | 0 | 0 | 0 | 345.5712 | 2073.4275 | DE27 | B
DE | DE244 | DEAG_BYHO-K0002 | DETP_BYHO-K0002 | KA Hof | 50.3334 | 11.9069 | 290000 | 284955 | YES | 1780.9688 | 5699.1 | 4274.325 | 8548.65 | 10329.6187 | 61977.7125 | DE24 | A
DE | DE249 | DEAG_BYHO-K0027 | DETP_BYHO-K0027 | Stammbach | 50.1419 | 11.6801 | 8000 | 2416 | NO | 15.1 | 0 | 0 | 0 | 87.58 | 525.48 | DE24 | A
DE | DE249 | DEAG_BYHO-K0052 | DETP_BYHO-K0052 | AV Selbitztal | 50.3499 | 11.7038 | 49999 | 33881 | YES | 211.7563 | 677.62 | 508.215 | 1016.43 | 1228.1863 | 7369.1175 | DE24 | C
DE | DE242 | DEAG_BYHO-K0089 | DETP_BYHO-K0089 | Bayreuth | 49.9575 | 11.5514 | 300000 | 271656 | YES | 1697.85 | 5433.12 | 4074.84 | 8149.68 | 9847.53 | 59085.18 | DE24 | A
DE | DE246 | DEAG_BYHO-K0093 | DETP_BYHO-K0093 | Bad Berneck im Fichtelgebirge | 50.0423 | 11.6403 | 13000 | 5873 | NO | 36.7063 | 0 | 0 | 0 | 212.8963 | 1277.3775 | DE24 | B
DE | DE246 | DEAG_BYHO-K0102 | DETP_BYHO-K0102 | Waischenfeld | 49.8369 | 11.3488 | 7500 | 7561 | NO | 47.2563 | 0 | 0 | 0 | 274.0863 | 1644.5175 | DE24 | C
DE | DE246 | DEAG_BYHO-K0104 | DETP_BYHO-K0104 | Mistelbach | 49.9172 | 11.5225 | 5000 | 3867 | NO | 24.1688 | 0 | 0 | 0 | 140.1788 | 841.0725 | DE24 | A
DE | DE246 | DEAG_BYHO-K0105 | DETP_BYHO-K0105 | Pegnitz | 49.7409 | 11.5551 | 16000 | 15062 | YES | 94.1375 | 301.24 | 225.93 | 451.86 | 545.9975 | 3275.985 | DE24 | B
DE | DE246 | DEAG_BYHO-K0106 | DETP_BYHO-K0106 | Hollfeld | 49.9288 | 11.2931 | 7000 | 4599 | NO | 28.7438 | 0 | 0 | 0 | 166.7138 | 1000.2825 | DE24 | B
DE | DE246 | DEAG_BYHO-K0111 | DETP_BYHO-K0111 | Pottenstein | 49.7755 | 11.4006 | 9500 | 8517 | NO | 53.2312 | 0 | 0 | 0 | 308.7412 | 1852.4475 | DE24 | A
DE | DE246 | DEAG_BYHO-K0117 | DETP_BYHO-K0117 | Gefrees | 50.0866 | 11.7227 | 7000 | 4272 | NO | 26.7 | 0 | 0 | 0 | 154.86 | 929.16 | DE24 | B
DE | DE246 | DEAG_BYHO-K0126 | DETP_BYHO-K0126 | Zweckverband zur Abwasserbeseitigung Truppachtal | 49.8995 | 11.3701 | 6300 | 6197 | NO | 38.7313 | 0 | 0 | 0 | 224.6412 | 1347.8475 | DE24 | C
DE | DE246 | DEAG_BYHO-K0133 | DETP_BYHO-K0133 | Verwaltungsgemeinschaft Betzenstein | 49.6508 | 11.4742 | 5400 | 3292 | NO | 20.575 | 0 | 0 | 0 | 119.335 | 716.01 | DE24 | B
DE | DE24B | DEAG_BYHO-K0150 | DETP_BYHO-K0150 | Marktleugast | 50.1531 | 11.636 | 7500 | 2841 | NO | 17.7563 | 0 | 0 | 0 | 102.9862 | 617.9175 | DE24 | A
DE | DE24B | DEAG_BYHO-K0157 | DETP_BYHO-K0157 | Himmelkron | 50.066 | 11.5859 | 11000 | 4748 | NO | 29.675 | 0 | 0 | 0 | 172.115 | 1032.69 | DE24 | B
DE | DE24B | DEAG_BYHO-K0162 | DETP_BYHO-K0162 | ZV Abwasserbeseitigung Rotmaintal | 50.0118 | 11.4838 | 9000 | 5783 | NO | 36.1438 | 0 | 0 | 0 | 209.6338 | 1257.8025 | DE24 | C
DE | DE24B | DEAG_BYHO-K0180 | DETP_BYHO-K0180 | Kulmbach | 50.1009 | 11.4197 | 270000 | 153516 | YES | 959.475 | 3070.32 | 2302.74 | 4605.48 | 5564.955 | 33389.73 | DE24 | A
DE | DE24D | DEAG_BYHO-K0196 | DETP_BYHO-K0196 | Arzberg | 50.0629 | 12.2024 | 24000 | 29714 | NO | 185.7125 | 0 | 0 | 0 | 1077.1325 | 6462.795 | DE24 | B
DE | DE24D | DEAG_BYHO-K0202 | DETP_BYHO-K0202 | gku Oberes Egertal Röslau | 50.089 | 11.985 | 16000 | 7047 | NO | 44.0437 | 0 | 0 | 0 | 255.4537 | 1532.7225 | DE24 | B
DE | DE24D | DEAG_BYHO-K0203 | DETP_BYHO-K0203 | Kirchenlamitz | 50.1727 | 11.9802 | 5000 | 3422 | NO | 21.3875 | 0 | 0 | 0 | 124.0475 | 744.285 | DE24 | C
DE | DE24D | DEAG_BYHO-K0204 | DETP_BYHO-K0204 | Marktleuthen | 50.1228 | 12.036 | 6000 | 2184 | NO | 13.65 | 0 | 0 | 0 | 79.17 | 475.02 | DE24 | C
DE | DE24D | DEAG_BYHO-K0205 | DETP_BYHO-K0205 | Wunsiedel | 50.0397 | 12.0274 | 35000 | 22548 | NO | 140.925 | 0 | 0 | 0 | 817.365 | 4904.19 | DE24 | B
DE | DE24D | DEAG_BYHO-K0206 | DETP_BYHO-K0206 | Selb | 50.1627 | 12.1173 | 65000 | 44200 | YES | 276.25 | 884 | 663 | 1326 | 1602.25 | 9613.5 | DE24 | B
DE | DE24D | DEAG_BYHO-K0207 | DETP_BYHO-K0207 | Marktredwitz | 50.0031 | 12.1101 | 60000 | 36088 | YES | 225.55 | 721.76 | 541.32 | 1082.64 | 1308.19 | 7849.14 | DE24 | A
DE | DE246 | DEAG_BYHO-K0208 | DETP_BYHO-K0208 | Bindlach | 50.0091 | 11.5793 | 14000 | 5693 | NO | 35.5813 | 0 | 0 | 0 | 206.3713 | 1238.2275 | DE24 | C
DE | DE211 | DEAG_BYIN-K0003 | DETP_BYIN-K0003 | ZV Zentralkläranlage Ingolstadt | 48.7612 | 11.4912 | 275000 | 194100 | YES | 1213.125 | 3882 | 2911.5 | 5823 | 7036.125 | 42216.75 | DE21 | A
DE | DE21J | DEAG_BYIN-K0004 | DETP_BYIN-K0004 | Pfaffenhofen/Ilm | 48.5432 | 11.5144 | 54000 | 49916 | YES | 311.975 | 998.32 | 748.74 | 1497.48 | 1809.455 | 10856.73 | DE21 | A
DE | DE21J | DEAG_BYIN-K0010 | DETP_BYIN-K0010 | Vohburg/Donau | 48.7707 | 11.6324 | 14000 | 11944 | NO | 74.65 | 0 | 0 | 0 | 432.97 | 2597.82 | DE21 | B
DE | DE21J | DEAG_BYIN-K0011 | DETP_BYIN-K0011 | Wolnzach | 48.6182 | 11.6059 | 15000 | 7214 | NO | 45.0875 | 0 | 0 | 0 | 261.5075 | 1569.045 | DE21 | B
DE | DE21J | DEAG_BYIN-K0013 | DETP_BYIN-K0013 | Münchsmünster | 48.7752 | 11.6974 | 12500 | 6295 | NO | 39.3438 | 0 | 0 | 0 | 228.1937 | 1369.1625 | DE21 | B
DE | DE21J | DEAG_BYIN-K0014 | DETP_BYIN-K0014 | ZV Mittleres Ilmtal Sitz Rohrbach | 48.6401 | 11.5841 | 10000 | 7603 | NO | 47.5188 | 0 | 0 | 0 | 275.6087 | 1653.6525 | DE21 | C
DE | DE21J | DEAG_BYIN-K0032 | DETP_BYIN-K0032 | ZV Oberes Ilmtal Sitz Reichertshausen | 48.4731 | 11.5035 | 17100 | 7183 | NO | 44.8938 | 0 | 0 | 0 | 260.3838 | 1562.3025 | DE21 | B
DE | DE21J | DEAG_BYIN-K0034 | DETP_BYIN-K0034 | Geisenfeld | 48.6947 | 11.6196 | 15000 | 8867 | NO | 55.4187 | 0 | 0 | 0 | 321.4287 | 1928.5725 | DE21 | B
DE | DE21J | DEAG_BYIN-K0035 | DETP_BYIN-K0035 | Manching | 48.723 | 11.4997 | 42000 | 25324 | YES | 158.275 | 506.48 | 379.86 | 759.72 | 917.995 | 5507.97 | DE21 | A
DE | DE219 | DEAG_BYIN-K0050 | DETP_BYIN-K0050 | Kipfenberg | 48.9558 | 11.3956 | 7500 | 6246 | NO | 39.0375 | 0 | 0 | 0 | 226.4175 | 1358.505 | DE21 | B
DE | DE219 | DEAG_BYIN-K0054 | DETP_BYIN-K0054 | Altmannstein | 48.9002 | 11.6582 | 7500 | 6583 | NO | 41.1438 | 0 | 0 | 0 | 238.6338 | 1431.8025 | DE21 | B
DE | DE219 | DEAG_BYIN-K0058 | DETP_BYIN-K0058 | Eichstätt | 48.8796 | 11.2167 | 30000 | 28468 | NO | 177.925 | 0 | 0 | 0 | 1031.965 | 6191.79 | DE21 | B
DE | DE219 | DEAG_BYIN-K0061 | DETP_BYIN-K0061 | Beilngries | 49.0277 | 11.4789 | 23000 | 10551 | NO | 65.9438 | 0 | 0 | 0 | 382.4738 | 2294.8425 | DE21 | A
DE | DE219 | DEAG_BYIN-K0094 | DETP_BYIN-K0094 | Pförring | 48.8082 | 11.6977 | 9800 | 7844 | NO | 49.025 | 0 | 0 | 0 | 284.345 | 1706.07 | DE21 | B
DE | DE21I | DEAG_BYIN-K0100 | DETP_BYIN-K0100 | Schrobenhausen | 48.5734 | 11.2769 | 55500 | 42390 | YES | 264.9375 | 847.8 | 635.85 | 1271.7 | 1536.6375 | 9219.825 | DE21 | A
DE | DE21I | DEAG_BYIN-K0108 | DETP_BYIN-K0108 | Neuburg/Donau | 48.7379 | 11.2079 | 67500 | 73859 | YES | 461.6188 | 1477.18 | 1107.885 | 2215.77 | 2677.3888 | 16064.3325 | DE21 | A
DE | DE21I | DEAG_BYIN-K0153 | DETP_BYIN-K0153 | Karlshuld | 48.6954 | 11.291 | 10000 | 12234 | NO | 76.4625 | 0 | 0 | 0 | 443.4825 | 2660.895 | DE21 | B
DE | DE219 | DEAG_BYIN-K0159 | DETP_BYIN-K0159 | Interpark Management Gmbh | 48.7843 | 11.5053 | 31000 | 20482 | NO | 128.0125 | 0 | 0 | 0 | 742.4725 | 4454.835 | DE21 | A
DE | DE241 | DEAG_BYKC-K0001 | DETP_BYKC-K0001 | Bamberg | 49.9122 | 10.8612 | 220000 | 161367 | YES | 1008.5437 | 3227.34 | 2420.505 | 4841.01 | 5849.5537 | 35097.3225 | DE24 | A
DE | DE245 | DEAG_BYKC-K0002 | DETP_BYKC-K0002 | Memmelsdorf | 49.9376 | 10.9468 | 14000 | 10683 | NO | 66.7687 | 0 | 0 | 0 | 387.2587 | 2323.5525 | DE24 | B
DE | DE245 | DEAG_BYKC-K0003 | DETP_BYKC-K0003 | Schlüsselfeld | 49.7451 | 10.6427 | 14000 | 9247 | NO | 57.7937 | 0 | 0 | 0 | 335.2037 | 2011.2225 | DE24 | C
DE | DE245 | DEAG_BYKC-K0011 | DETP_BYKC-K0011 | Scheßlitz | 49.9714 | 11.0208 | 10000 | 5138 | NO | 32.1125 | 0 | 0 | 0 | 186.2525 | 1117.515 | DE24 | B
DE | DE245 | DEAG_BYKC-K0014 | DETP_BYKC-K0014 | Baunach | 49.9828 | 10.858 | 6500 | 6620 | NO | 41.375 | 0 | 0 | 0 | 239.975 | 1439.85 | DE24 | B
DE | DE245 | DEAG_BYKC-K0016 | DETP_BYKC-K0016 | AZV BUTTENHEIM-ALTENDORF | 49.8033 | 10.993 | 13000 | 11865 | NO | 74.1562 | 0 | 0 | 0 | 430.1062 | 2580.6375 | DE24 | B
DE | DE245 | DEAG_BYKC-K0017 | DETP_BYKC-K0017 | Viereth-Trunstadt | 49.935 | 10.7512 | 6000 | 6150 | NO | 38.4375 | 0 | 0 | 0 | 222.9375 | 1337.625 | DE24 | B
DE | DE245 | DEAG_BYKC-K0018 | DETP_BYKC-K0018 | Burgebrach | 49.8301 | 10.7568 | 13000 | 8840 | NO | 55.25 | 0 | 0 | 0 | 320.45 | 1922.7 | DE24 | A
DE | DE245 | DEAG_BYKC-K0020 | DETP_BYKC-K0020 | Heiligenstadt in Oberfranken | 49.8525 | 11.1812 | 6000 | 2264 | NO | 14.15 | 0 | 0 | 0 | 82.07 | 492.42 | DE24 | C
DE | DE245 | DEAG_BYKC-K0022 | DETP_BYKC-K0022 | Lisberg | 49.8909 | 10.7316 | 8000 | 3163 | NO | 19.7688 | 0 | 0 | 0 | 114.6587 | 687.9525 | DE24 | B
DE | DE245 | DEAG_BYKC-K0025 | DETP_BYKC-K0025 | Hirschaid | 49.8211 | 10.9639 | 16000 | 17060 | NO | 106.625 | 0 | 0 | 0 | 618.425 | 3710.55 | DE24 | C
DE | DE245 | DEAG_BYKC-K0029 | DETP_BYKC-K0029 | Stegaurach | 49.8524 | 10.8677 | 9000 | 7205 | NO | 45.0312 | 0 | 0 | 0 | 261.1812 | 1567.0875 | DE24 | B
DE | DE245 | DEAG_BYKC-K0030 | DETP_BYKC-K0030 | Strullendorf | 49.8438 | 10.9544 | 15000 | 9449 | NO | 59.0563 | 0 | 0 | 0 | 342.5263 | 2055.1575 | DE24 | A
DE | DE245 | DEAG_BYKC-K0031 | DETP_BYKC-K0031 | Oberhaid | 49.9314 | 10.7903 | 5000 | 3486 | NO | 21.7875 | 0 | 0 | 0 | 126.3675 | 758.205 | DE24 | B
DE | DE245 | DEAG_BYKC-K0032 | DETP_BYKC-K0032 | ZV Pommersfelden-Frensdorf-Süd | 49.7824 | 10.849 | 5500 | 3071 | NO | 19.1938 | 0 | 0 | 0 | 111.3237 | 667.9425 | DE24 | B
DE | DE245 | DEAG_BYKC-K0033 | DETP_BYKC-K0033 | Breitengüßbach | 49.9791 | 10.8853 | 6850 | 5270 | NO | 32.9375 | 0 | 0 | 0 | 191.0375 | 1146.225 | DE24 | B
DE | DE245 | DEAG_BYKC-K0036 | DETP_BYKC-K0036 | Zapfendorf | 50.0193 | 10.9251 | 7300 | 5200 | NO | 32.5 | 0 | 0 | 0 | 188.5 | 1131 | DE24 | A
DE | DE248 | DEAG_BYKC-K0045 | DETP_BYKC-K0045 | Gößweinstein | 49.7754 | 11.3374 | 6000 | 3900 | NO | 24.375 | 0 | 0 | 0 | 141.375 | 848.25 | DE24 | B
DE | DE248 | DEAG_BYKC-K0047 | DETP_BYKC-K0047 | ZV_Hirtenbachgruppe | 49.6959 | 11.0449 | 10000 | 7994 | NO | 49.9625 | 0 | 0 | 0 | 289.7825 | 1738.695 | DE24 | B
DE | DE248 | DEAG_BYKC-K0050 | DETP_BYKC-K0050 | Ebermannstadt | 49.7749 | 11.1791 | 25000 | 22510 | NO | 140.6875 | 0 | 0 | 0 | 815.9875 | 4895.925 | DE24 | B
DE | DE248 | DEAG_BYKC-K0051 | DETP_BYKC-K0051 | ZV_Eggolsheim_Hallerndorf | 49.7836 | 11.0161 | 15000 | 19495 | NO | 121.8438 | 0 | 0 | 0 | 706.6937 | 4240.1625 | DE24 | C
DE | DE248 | DEAG_BYKC-K0052 | DETP_BYKC-K0052 | ZV Trubachtal Egloffstein | 49.7188 | 11.25 | 7400 | 9565 | NO | 59.7812 | 0 | 0 | 0 | 346.7312 | 2080.3875 | DE24 | C
DE | DE248 | DEAG_BYKC-K0053 | DETP_BYKC-K0053 | Forchheim | 49.7416 | 11.0457 | 90000 | 69250 | YES | 432.8125 | 1385 | 1038.75 | 2077.5 | 2510.3125 | 15061.875 | DE24 | B
DE | DE248 | DEAG_BYKC-K0054 | DETP_BYKC-K0054 | ZV Obere Schwabach | 49.5938 | 11.2015 | 27500 | 15709 | NO | 98.1812 | 0 | 0 | 0 | 569.4512 | 3416.7075 | DE24 | B
DE | DE24C | DEAG_BYKC-K0056 | DETP_BYKC-K0056 | Redwitz/Rodach | 50.1734 | 11.1956 | 15000 | 10200 | NO | 63.75 | 0 | 0 | 0 | 369.75 | 2218.5 | DE24 | B
DE | DE24C | DEAG_BYKC-K0058 | DETP_BYKC-K0058 | Weismain | 50.1056 | 11.2409 | 20000 | 13600 | NO | 85 | 0 | 0 | 0 | 493 | 2958 | DE24 | C
DE | DE24C | DEAG_BYKC-K0061 | DETP_BYKC-K0061 | Ebensfeld | 50.0591 | 10.9476 | 9950 | 6468 | NO | 40.425 | 0 | 0 | 0 | 234.465 | 1406.79 | DE24 | B
DE | DE24C | DEAG_BYKC-K0063 | DETP_BYKC-K0063 | AZV Kunstadt | 50.1426 | 11.2326 | 20000 | 13600 | NO | 85 | 0 | 0 | 0 | 493 | 2958 | DE24 | A
DE | DE24C | DEAG_BYKC-K0064 | DETP_BYKC-K0064 | ZV Marktzeuln-Michelau Sitz Michelau | 50.1569 | 11.1029 | 14717 | 10008 | NO | 62.55 | 0 | 0 | 0 | 362.79 | 2176.74 | DE24 | B
DE | DE24C | DEAG_BYKC-K0074 | DETP_BYKC-K0074 | Bad Staffelstein | 50.0988 | 10.9726 | 26000 | 17680 | NO | 110.5 | 0 | 0 | 0 | 640.9 | 3845.4 | DE24 | C
DE | DE24C | DEAG_BYKC-K0075 | DETP_BYKC-K0075 | Lichtenfels | 50.1419 | 11.0494 | 40000 | 27200 | YES | 170 | 544 | 408 | 816 | 986 | 5916 | DE24 | A
DE | DE243 | DEAG_BYKC-K0083 | DETP_BYKC-K0083 | Coburg | 50.2408 | 10.9695 | 150000 | 108000 | YES | 675 | 2160 | 1620 | 3240 | 3915 | 23490 | DE24 | A
DE | DE247 | DEAG_BYKC-K0086 | DETP_BYKC-K0086 | Weitramsdorf | 50.2189 | 10.8413 | 8000 | 5200 | NO | 32.5 | 0 | 0 | 0 | 188.5 | 1131 | DE24 | C
DE | DE247 | DEAG_BYKC-K0087 | DETP_BYKC-K0087 | Ebersdorf | 50.2112 | 11.0922 | 9500 | 6175 | NO | 38.5938 | 0 | 0 | 0 | 223.8438 | 1343.0625 | DE24 | B
DE | DE247 | DEAG_BYKC-K0093 | DETP_BYKC-K0093 | Sonnefeld | 50.2148 | 11.1415 | 7000 | 4550 | NO | 28.4375 | 0 | 0 | 0 | 164.9375 | 989.625 | DE24 | A
DE | DE247 | DEAG_BYKC-K0094 | DETP_BYKC-K0094 | Meeder | 50.2971 | 10.9278 | 5000 | 3450 | NO | 21.5625 | 0 | 0 | 0 | 125.0625 | 750.375 | DE24 | C
DE | DE247 | DEAG_BYKC-K0098 | DETP_BYKC-K0098 | Weidhausen | 50.2012 | 11.1259 | 6000 | 3900 | NO | 24.375 | 0 | 0 | 0 | 141.375 | 848.25 | DE24 | A
DE | DE247 | DEAG_BYKC-K0099 | DETP_BYKC-K0099 | Itzgrund | 50.1155 | 10.8682 | 11000 | 7480 | NO | 46.75 | 0 | 0 | 0 | 271.15 | 1626.9 | DE24 | C
DE | DE247 | DEAG_BYKC-K0100 | DETP_BYKC-K0100 | Mittlerer Itzgrund | 50.2112 | 10.9813 | 20000 | 13600 | NO | 85 | 0 | 0 | 0 | 493 | 2958 | DE24 | B
DE | DE247 | DEAG_BYKC-K0101 | DETP_BYKC-K0101 | Neustadt/Cbg. | 50.3201 | 11.1105 | 30000 | 20400 | NO | 127.5 | 0 | 0 | 0 | 739.5 | 4437 | DE24 | A
DE | DE247 | DEAG_BYKC-K0102 | DETP_BYKC-K0102 | Rödental | 50.2817 | 11.0168 | 35000 | 23800 | NO | 148.75 | 0 | 0 | 0 | 862.75 | 5176.5 | DE24 | B
DE | DE247 | DEAG_BYKC-K0103 | DETP_BYKC-K0103 | Bad Rodach | 50.3313 | 10.7922 | 12000 | 8160 | NO | 51 | 0 | 0 | 0 | 295.8 | 1774.8 | DE24 | B
DE | DE24A | DEAG_BYKC-K0104 | DETP_BYKC-K0104 | Kronach | 50.2245 | 11.3166 | 28000 | 21502 | NO | 134.3875 | 0 | 0 | 0 | 779.4475 | 4676.685 | DE24 | A
DE | DE24A | DEAG_BYKC-K0105 | DETP_BYKC-K0105 | Ludwigsstadt | 50.4917 | 11.3784 | 14000 | 6667 | NO | 41.6688 | 0 | 0 | 0 | 241.6787 | 1450.0725 | DE24 | A
DE | DE24A | DEAG_BYKC-K0107 | DETP_BYKC-K0107 | Wallenfels | 50.2769 | 11.4393 | 8750 | 2317 | NO | 14.4813 | 0 | 0 | 0 | 83.9912 | 503.9475 | DE24 | C
DE | DE24A | DEAG_BYKC-K0111 | DETP_BYKC-K0111 | Kronach-Nord | 50.2648 | 11.3044 | 10000 | 7827 | NO | 48.9187 | 0 | 0 | 0 | 283.7287 | 1702.3725 | DE24 | A
DE | DE24A | DEAG_BYKC-K0116 | DETP_BYKC-K0116 | Steinwiesen | 50.2881 | 11.4454 | 9000 | 2934 | NO | 18.3375 | 0 | 0 | 0 | 106.3575 | 638.145 | DE24 | C
DE | DE24A | DEAG_BYKC-K0118 | DETP_BYKC-K0118 | Ölsnitz-Rodachtal | 50.3553 | 11.5129 | 6000 | 5637 | NO | 35.2313 | 0 | 0 | 0 | 204.3413 | 1226.0475 | DE24 | C
DE | DE24A | DEAG_BYKC-K0120 | DETP_BYKC-K0120 | Steinachtal | 50.2359 | 11.1987 | 13000 | 9150 | NO | 57.1875 | 0 | 0 | 0 | 331.6875 | 1990.125 | DE24 | C
DE | DE24A | DEAG_BYKC-K0121 | DETP_BYKC-K0121 | Kronach-Süd | 50.1866 | 11.2511 | 25000 | 20713 | NO | 129.4563 | 0 | 0 | 0 | 750.8463 | 4505.0775 | DE24 | B
DE | DE24A | DEAG_BYKC-K0126 | DETP_BYKC-K0126 | Pressig | 50.3394 | 11.2983 | 9750 | 2599 | NO | 16.2438 | 0 | 0 | 0 | 94.2138 | 565.2825 | DE24 | B
DE | DE24A | DEAG_BYKC-K0130 | DETP_BYKC-K0130 | Marktrodach | 50.2366 | 11.38 | 6000 | 2773 | NO | 17.3313 | 0 | 0 | 0 | 100.5213 | 603.1275 | DE24 | C
DE | DE272 | DEAG_BYKE-K0001 | DETP_BYKE-K0001 | Kaufbeuren | 47.9025 | 10.6151 | 80000 | 58748 | YES | 367.175 | 1174.96 | 881.22 | 1762.44 | 2129.615 | 12777.69 | DE27 | A
DE | DE27E | DEAG_BYKE-K0016 | DETP_BYKE-K0016 | ZV Obere Iller Sitz Sonthofen | 47.5994 | 10.2652 | 150000 | 136131 | YES | 850.8188 | 2722.62 | 2041.965 | 4083.93 | 4934.7487 | 29608.4925 | DE27 | C
DE | DE27E | DEAG_BYKE-K0017 | DETP_BYKE-K0017 | Oberstaufen | 47.5337 | 9.9878 | 18750 | 13293 | NO | 83.0812 | 0 | 0 | 0 | 481.8712 | 2891.2275 | DE27 | C
DE | DE27E | DEAG_BYKE-K0018 | DETP_BYKE-K0018 | Oy- Mittelberg | 47.6458 | 10.4667 | 5500 | 2886 | NO | 18.0375 | 0 | 0 | 0 | 104.6175 | 627.705 | DE27 | B
DE | DE27E | DEAG_BYKE-K0020 | DETP_BYKE-K0020 | Kempten AZV | 47.7793 | 10.2868 | 350000 | 450300 | YES | 2814.375 | 9006 | 6754.5 | 13509 | 16323.375 | 97940.25 | DE27 | C
DE | DE27E | DEAG_BYKE-K0028 | DETP_BYKE-K0028 | Wertach | 47.606 | 10.4272 | 7500 | 3831 | NO | 23.9437 | 0 | 0 | 0 | 138.8737 | 833.2425 | DE27 | C
DE | DE27B | DEAG_BYKE-K0032 | DETP_BYKE-K0032 | Marktoberdorf | 47.7963 | 10.619 | 46300 | 48831 | YES | 305.1938 | 976.62 | 732.465 | 1464.93 | 1770.1237 | 10620.7425 | DE27 | A
DE | DE27B | DEAG_BYKE-K0041 | DETP_BYKE-K0041 | Buchloe | 48.0445 | 10.7209 | 30000 | 32786 | NO | 204.9125 | 0 | 0 | 0 | 1188.4925 | 7130.955 | DE27 | A
DE | DE27B | DEAG_BYKE-K0043 | DETP_BYKE-K0043 | Nesselwang | 47.6321 | 10.501 | 7000 | 3920 | NO | 24.5 | 0 | 0 | 0 | 142.1 | 852.6 | DE27 | B
DE | DE27B | DEAG_BYKE-K0044 | DETP_BYKE-K0044 | ZV Füssen Sitz Füssen | 47.5983 | 10.7118 | 70000 | 34520 | YES | 215.75 | 690.4 | 517.8 | 1035.6 | 1251.35 | 7508.1 | DE27 | C
DE | DE27B | DEAG_BYKE-K0055 | DETP_BYKE-K0055 | Obergünzburg | 47.8536 | 10.4155 | 15000 | 11867 | NO | 74.1688 | 0 | 0 | 0 | 430.1787 | 2581.0725 | DE27 | B
DE | DE27B | DEAG_BYKE-K0062 | DETP_BYKE-K0062 | ZV Gennach-Kirchweihtal S. Westendorf | 47.9583 | 10.7287 | 8000 | 6734 | NO | 42.0875 | 0 | 0 | 0 | 244.1075 | 1464.645 | DE27 | C
DE | DE27B | DEAG_BYKE-K0063 | DETP_BYKE-K0063 | Halblech | 47.6462 | 10.8003 | 7500 | 3119 | NO | 19.4938 | 0 | 0 | 0 | 113.0638 | 678.3825 | DE27 | C
DE | DE27B | DEAG_BYKE-K0064 | DETP_BYKE-K0064 | ZV Aitrang-Ruderatshofen Sitz Ruderatsh. | 47.8254 | 10.5929 | 6000 | 5124 | NO | 32.025 | 0 | 0 | 0 | 185.745 | 1114.47 | DE27 | C
DE | DE27B | DEAG_BYKE-K0065 | DETP_BYKE-K0065 | ZV Wertach Ost Sitz Germaringen | 47.944 | 10.6281 | 13600 | 9203 | NO | 57.5188 | 0 | 0 | 0 | 333.6087 | 2001.6525 | DE27 | C
DE | DE27A | DEAG_BYKE-K0074 | DETP_BYKE-K0074 | Abwasserverband Obere Leiblach | 47.6413 | 9.8262 | 34375 | 26012 | NO | 162.575 | 0 | 0 | 0 | 942.935 | 5657.61 | DE27 | A
DE | DE27A |  | DETP_BYKE-K0079 | Lindau/Bodensee | 47.5459 | 9.7329 | 60000 | 60000 | YES | 375 | 1200 | 900 | 1800 | 2175 | 13050 | DE27 | A
DE | DE27A | DEAG_BYKE-K0081 | DETP_BYKE-K0081 | ZV Rothach S.Lindenberg | 47.5742 | 9.904 | 77500 | 34500 | YES | 215.625 | 690 | 517.5 | 1035 | 1250.625 | 7503.75 | DE27 | A
DE | DE27A | DEAG_BYKE-K0087 | DETP_BYKE-K0087 | Grünenbach | 47.6195 | 9.9875 | 11250 | 8576 | NO | 53.6 | 0 | 0 | 0 | 310.88 | 1865.28 | DE27 | C
DE | DE27B | DEAG_BYKE-K0094 | DETP_BYKE-K0094 | Ronsberg | 47.9079 | 10.4052 | 6000 | 4851 | NO | 30.3187 | 0 | 0 | 0 | 175.8487 | 1055.0925 | DE27 | C
DE | DE274 | DEAG_BYKE-K0112 | DETP_BYKE-K0112 | Memmingen | 48.0529 | 10.1439 | 230000 | 118801 | YES | 742.5063 | 2376.02 | 1782.015 | 3564.03 | 4306.5363 | 25839.2175 | DE27 | C
DE | DE27C | DEAG_BYKE-K0115 | DETP_BYKE-K0115 | Kammlach OT Unterkammlach | 48.0651 | 10.4185 | 9950 | 7941 | NO | 49.6313 | 0 | 0 | 0 | 287.8612 | 1727.1675 | DE27 | B
DE | DE27C | DEAG_BYKE-K0116 | DETP_BYKE-K0116 | Mindelheim | 48.0647 | 10.4843 | 47000 | 26015 | YES | 162.5938 | 520.3 | 390.225 | 780.45 | 943.0437 | 5658.2625 | DE27 | C
DE | DE27C | DEAG_BYKE-K0120 | DETP_BYKE-K0120 | Babenhausen | 48.1549 | 10.2395 | 9500 | 4700 | NO | 29.375 | 0 | 0 | 0 | 170.375 | 1022.25 | DE27 | B
DE | DE27C | DEAG_BYKE-K0123 | DETP_BYKE-K0123 | Oberschönegg | 48.1073 | 10.2905 | 44000 | 34570 | NO | 216.0625 | 0 | 0 | 0 | 1253.1625 | 7518.975 | DE27 | C
DE | DE27C | DEAG_BYKE-K0124 | DETP_BYKE-K0124 | Kirchheim/Schwaben | 48.1864 | 10.4649 | 7000 | 2866 | NO | 17.9125 | 0 | 0 | 0 | 103.8925 | 623.355 | DE27 | B
DE | DE27C | DEAG_BYKE-K0130 | DETP_BYKE-K0130 | VG Ottobeuren-Hawangen | 47.9763 | 10.2862 | 20000 | 19591 | NO | 122.4438 | 0 | 0 | 0 | 710.1738 | 4261.0425 | DE27 | C
DE | DE27C | DEAG_BYKE-K0131 | DETP_BYKE-K0131 | Türkheim-Vg | 48.0795 | 10.6558 | 18000 | 11334 | NO | 70.8375 | 0 | 0 | 0 | 410.8575 | 2465.145 | DE27 | C
DE | DE27C | DEAG_BYKE-K0132 | DETP_BYKE-K0132 | Illerwinkel-Vg | 47.9092 | 10.1173 | 7200 | 6600 | NO | 41.25 | 0 | 0 | 0 | 239.25 | 1435.5 | DE27 | B
DE | DE27C | DEAG_BYKE-K0134 | DETP_BYKE-K0134 | Ettringen | 48.1178 | 10.6648 | 6000 | 4344 | NO | 27.15 | 0 | 0 | 0 | 157.47 | 944.82 | DE27 | A
DE | DE27C | DEAG_BYKE-K0138 | DETP_BYKE-K0138 | ZV Oberes Günztal | 48.0818 | 10.2982 | 25000 | 14950 | NO | 93.4375 | 0 | 0 | 0 | 541.9375 | 3251.625 | DE27 | C
DE | DE27C | DEAG_BYKE-K0139 | DETP_BYKE-K0139 | Bad Wörishofen | 48.041 | 10.5971 | 43000 | 34100 | YES | 213.125 | 682 | 511.5 | 1023 | 1236.125 | 7416.75 | DE27 | C
DE | DE27B | DEAG_BYKE-K0151 | DETP_BYKE-K0151 | AV Lechbruck-Bernbeuren | 47.718 | 10.827 | 11000 | 6742 | NO | 42.1375 | 0 | 0 | 0 | 244.3975 | 1466.385 | DE27 | C
DE | DE262 | DEAG_BYKG-K0001 | DETP_BYKG-K0001 | KA Schweinfurt | 50.0249 | 10.211 | 250000 | 168787 | YES | 1054.9188 | 3375.74 | 2531.805 | 5063.61 | 6118.5288 | 36711.1725 | DE26 | A
DE | DE265 | DEAG_BYKG-K0003 | DETP_BYKG-K0003 | ZV Aschach-Saale Sitz Burkardroth | 50.2414 | 10.065 | 19500 | 14617 | NO | 91.3563 | 0 | 0 | 0 | 529.8662 | 3179.1975 | DE26 | B
DE | DE265 | DEAG_BYKG-K0009 | DETP_BYKG-K0009 | Bad Kissingen | 50.1809 | 10.0739 | 60000 | 37850 | YES | 236.5625 | 757 | 567.75 | 1135.5 | 1372.0625 | 8232.375 | DE26 | A
DE | DE265 | DEAG_BYKG-K0011 | DETP_BYKG-K0011 | Münnerstadt | 50.2598 | 10.1857 | 9500 | 6240 | NO | 39 | 0 | 0 | 0 | 226.2 | 1357.2 | DE26 | C
DE | DE265 | DEAG_BYKG-K0021 | DETP_BYKG-K0021 | Wildflecken | 50.3694 | 9.8974 | 9900 | 4133 | NO | 25.8313 | 0 | 0 | 0 | 149.8212 | 898.9275 | DE26 | C
DE | DE265 | DEAG_BYKG-K0033 | DETP_BYKG-K0033 | ZV Obere Lauer Sitz Maßbach | 50.2311 | 10.2435 | 17000 | 12755 | NO | 79.7188 | 0 | 0 | 0 | 462.3687 | 2774.2125 | DE26 | C
DE | DE265 | DEAG_BYKG-K0034 | DETP_BYKG-K0034 | ZV Thulba-Saale Sitz Hammelburg | 50.1183 | 9.8769 | 28000 | 21754 | NO | 135.9625 | 0 | 0 | 0 | 788.5825 | 4731.495 | DE26 | A
DE | DE265 | DEAG_BYKG-K0035 | DETP_BYKG-K0035 | Bad Brückenau | 50.2677 | 9.705 | 20000 | 10767 | NO | 67.2938 | 0 | 0 | 0 | 390.3037 | 2341.8225 | DE26 | A
DE | DE266 | DEAG_BYKG-K0039 | DETP_BYKG-K0039 | Saal a.d. Saale | 50.3313 | 10.3246 | 7000 | 4550 | NO | 28.4375 | 0 | 0 | 0 | 164.9375 | 989.625 | DE26 | B
DE | DE266 | DEAG_BYKG-K0068 | DETP_BYKG-K0068 | Bischofsheim/Rhön | 50.4006 | 10.0503 | 9900 | 7725 | NO | 48.2812 | 0 | 0 | 0 | 280.0312 | 1680.1875 | DE26 | C
DE | DE266 | DEAG_BYKG-K0077 | DETP_BYKG-K0077 | ZV Saale-Lauer Sitz Hohenroth | 50.3038 | 10.1741 | 40000 | 34905 | YES | 218.1562 | 698.1 | 523.575 | 1047.15 | 1265.3062 | 7591.8375 | DE26 | C
DE | DE266 | DEAG_BYKG-K0078 | DETP_BYKG-K0078 | ZV Elstal | 50.3807 | 10.2284 | 10000 | 6147 | NO | 38.4188 | 0 | 0 | 0 | 222.8288 | 1336.9725 | DE26 | C
DE | DE266 | DEAG_BYKG-K0080 | DETP_BYKG-K0080 | Bad Königshofen | 50.2951 | 10.4479 | 15000 | 9398 | NO | 58.7375 | 0 | 0 | 0 | 340.6775 | 2044.065 | DE26 | B
DE | DE266 | DEAG_BYKG-K0081 | DETP_BYKG-K0081 | ZV Mellrichstädter Gruppe S. Mellrichstadt | 50.4198 | 10.2985 | 24000 | 11498 | NO | 71.8625 | 0 | 0 | 0 | 416.8025 | 2500.815 | DE26 | A
DE | DE266 | DEAG_BYKG-K0083 | DETP_BYKG-K0083 | ZV Obere Streu Sitz Fladungen | 50.4694 | 10.1914 | 9000 | 7244 | NO | 45.275 | 0 | 0 | 0 | 262.595 | 1575.57 | DE26 | C
DE | DE26B | DEAG_BYKG-K0085 | DETP_BYKG-K0085 | Bergrheinfeld | 49.9895 | 10.171 | 17000 | 13836 | NO | 86.475 | 0 | 0 | 0 | 501.555 | 3009.33 | DE26 | C
DE | DE26B | DEAG_BYKG-K0099 | DETP_BYKG-K0099 | Werneck | 49.9645 | 10.061 | 18000 | 12403 | NO | 77.5187 | 0 | 0 | 0 | 449.6087 | 2697.6525 | DE26 | C
DE | DE26B | DEAG_BYKG-K0100 | DETP_BYKG-K0100 | Gerolzhofen | 49.9097 | 10.3379 | 14000 | 12397 | NO | 77.4813 | 0 | 0 | 0 | 449.3912 | 2696.3475 | DE26 | B
DE | DE26B | DEAG_BYKG-K0123 | DETP_BYKG-K0123 | ZV Unterer Unkenbach Sitz Schwebheim | 49.9632 | 10.1963 | 13000 | 8302 | NO | 51.8875 | 0 | 0 | 0 | 300.9475 | 1805.685 | DE26 | B
DE | DE26B | DEAG_BYKG-K0124 | DETP_BYKG-K0124 | ZV Obere Werntalgemeinden S. Poppenhausen | 50.0397 | 10.1752 | 50000 | 19316 | YES | 120.725 | 386.32 | 289.74 | 579.48 | 700.205 | 4201.23 | DE26 | B
DE | DE267 | DEAG_BYKG-K0130 | DETP_BYKG-K0130 | ZV Raum Theres Sitz Gädheim | 50.0196 | 10.3522 | 6700 | 5400 | NO | 33.75 | 0 | 0 | 0 | 195.75 | 1174.5 | DE26 | B
DE | DE267 | DEAG_BYKG-K0176 | DETP_BYKG-K0176 | ZV Raum Eltmann- Ebelsbach S. Eltmann | 49.9881 | 10.6498 | 25000 | 8868 | NO | 55.425 | 0 | 0 | 0 | 321.465 | 1928.79 | DE26 | B
DE | DE267 | DEAG_BYKG-K0181 | DETP_BYKG-K0181 | Hofheim/Ufr. | 50.1352 | 10.5305 | 15000 | 10074 | NO | 62.9625 | 0 | 0 | 0 | 365.1825 | 2191.095 | DE26 | B
DE | DE267 | DEAG_BYKG-K0182 | DETP_BYKG-K0182 | Ebern | 50.079 | 10.8005 | 18000 | 8849 | NO | 55.3063 | 0 | 0 | 0 | 320.7763 | 1924.6575 | DE26 | C
DE | DE267 | DEAG_BYKG-K0183 | DETP_BYKG-K0183 | Knetzgau | 50.0061 | 10.5305 | 19000 | 14422 | NO | 90.1375 | 0 | 0 | 0 | 522.7975 | 3136.785 | DE26 | C
DE | DE267 | DEAG_BYKG-K0184 | DETP_BYKG-K0184 | Haßfurt | 50.0313 | 10.4931 | 27500 | 26321 | NO | 164.5062 | 0 | 0 | 0 | 954.1363 | 5724.8175 | DE26 | A
DE | DE267 | DEAG_BYKG-K0185 | DETP_BYKG-K0185 | Zeil/Sand a. Main | 50.0043 | 10.5935 | 19500 | 16433 | NO | 102.7063 | 0 | 0 | 0 | 595.6962 | 3574.1775 | DE26 | A
DE | DE266 | DEAG_BYKG-K0192 | DETP_BYKG-K0192 | ZV Streu-Saale Sitz Heustreu | 50.3445 | 10.2624 | 7300 | 5797 | NO | 36.2313 | 0 | 0 | 0 | 210.1413 | 1260.8475 | DE26 | C
DE | DE265 | DEAG_BYKG-K0196 | DETP_BYKG-K0196 | Nüdlingen | 50.2238 | 10.1021 | 6850 | 3834 | NO | 23.9625 | 0 | 0 | 0 | 138.9825 | 833.895 | DE26 | C
DE | DE26B | DEAG_BYKG-K10100 | DETP_BYKG-K10100 | ZV Kolitzheim-Sulzheim | 49.9068 | 10.2704 | 7200 | 6214 | NO | 38.8375 | 0 | 0 | 0 | 225.2575 | 1351.545 | DE26 | C
DE | DE276 | DEAG_BYDON-K0041 | DETP_BYDON-K0041 | Altenmünster | 48.4909 | 10.6118 | 8500 | 4047 | NO | 25.2938 | 0 | 0 | 0 | 146.7038 | 880.2225 | DE27 | B
DE | DE276 | DEAG_BYDON-K0042 | DETP_BYDON-K0042 | AZV Schmuttertal Sitz Hirblingen | 48.4391 | 10.8253 | 50000 | 52300 | YES | 326.875 | 1046 | 784.5 | 1569 | 1895.875 | 11375.25 | DE27 | C
DE | DE27D | DEAG_BYDON-K0048 | DETP_BYDON-K0048 | Oettingen/Bay | 48.9418 | 10.6075 | 9400 | 11700 | NO | 73.125 | 0 | 0 | 0 | 424.125 | 2544.75 | DE27 | A
DE | DE27D | DEAG_BYDON-K0062 | DETP_BYDON-K0062 | Donauwörth | 48.7109 | 10.7959 | 64000 | 32917 | YES | 205.7313 | 658.34 | 493.755 | 987.51 | 1193.2413 | 7159.4475 | DE27 | A
DE | DE27D | DEAG_BYDON-K0070 | DETP_BYDON-K0070 | Rain/Lech | 48.699 | 10.9231 | 21000 | 13427 | NO | 83.9188 | 0 | 0 | 0 | 486.7287 | 2920.3725 | DE27 | B
DE | DE27D | DEAG_BYDON-K0079 | DETP_BYDON-K0079 | Tapfheim OT Erlingshofen | 48.6814 | 10.7154 | 6000 | 4966 | NO | 31.0375 | 0 | 0 | 0 | 180.0175 | 1080.105 | DE27 | B
DE | DE27D | DEAG_BYDON-K0082 | DETP_BYDON-K0082 | Harburg/Schwaben | 48.7748 | 10.7072 | 7500 | 5835 | NO | 36.4688 | 0 | 0 | 0 | 211.5187 | 1269.1125 | DE27 | B
DE | DE27D | DEAG_BYDON-K0084 | DETP_BYDON-K0084 | Kaisheim | 48.7598 | 10.7874 | 6000 | 3900 | NO | 24.375 | 0 | 0 | 0 | 141.375 | 848.25 | DE27 | C
DE | DE27D | DEAG_BYDON-K0087 | DETP_BYDON-K0087 | Monheim | 48.8392 | 10.8692 | 9700 | 5213 | NO | 32.5813 | 0 | 0 | 0 | 188.9713 | 1133.8275 | DE27 | B
DE | DE27D | DEAG_BYDON-K0093 | DETP_BYDON-K0093 | Nördlingen | 48.8735 | 10.5124 | 70000 | 32894 | YES | 205.5875 | 657.88 | 493.41 | 986.82 | 1192.4075 | 7154.445 | DE27 | A
DE | DE275 | DEAG_BYDON-K0139 | DETP_BYDON-K0139 | Baar (Schwaben) | 48.6001 | 10.9525 | 9000 | 5850 | NO | 36.5625 | 0 | 0 | 0 | 212.0625 | 1272.375 | DE27 | C
DE | DE227 | DEAG_BYLA-K0075 | DETP_BYLA-K0075 | Rottenburg/Laaber | 48.7135 | 12.0148 | 25000 | 17744 | NO | 110.9 | 0 | 0 | 0 | 643.22 | 3859.32 | DE22 | A
DE | DE227 | DEAG_BYLA-K0076 | DETP_BYLA-K0076 | Bruckberg | 48.5066 | 12.0155 | 6350 | 4776 | NO | 29.85 | 0 | 0 | 0 | 173.13 | 1038.78 | DE22 | B
DE | DE227 | DEAG_BYLA-K0091 | DETP_BYLA-K0091 | Buch am Erlbach | 48.4628 | 12.0114 | 5000 | 2621 | NOT KNOWN | 16.3813 | 0 | 0 | 0 | 95.0113 | 570.0675 | DE22 | B
DE | DE227 | DEAG_BYLA-K0092 | DETP_BYLA-K0092 | Essenbach | 48.6099 | 12.2921 | 15000 | 9011 | NO | 56.3188 | 0 | 0 | 0 | 326.6488 | 1959.8925 | DE22 | A
DE | DE227 | DEAG_BYLA-K0098 | DETP_BYLA-K0098 | ZV AW Niederaichbach-Wörth S. Niederaichb. | 48.6179 | 12.3506 | 12000 | 13117 | NO | 81.9813 | 0 | 0 | 0 | 475.4912 | 2852.9475 | DE22 | B
DE | DE227 | DEAG_BYLA-K0101 | DETP_BYLA-K0101 | Vilsbiburg | 48.464 | 12.3759 | 16716 | 14982 | NO | 93.6375 | 0 | 0 | 0 | 543.0975 | 3258.585 | DE22 | C
DE | DE22C | DEAG_BYLA-K0106 | DETP_BYLA-K0106 | Landau/Isar | 48.6777 | 12.7057 | 40000 | 27107 | YES | 169.4188 | 542.14 | 406.605 | 813.21 | 982.6288 | 5895.7725 | DE22 | B
DE | DE22C | DEAG_BYLA-K0109 | DETP_BYLA-K0109 | Mamming | 48.6568 | 12.6129 | 6660 | 3878 | NO | 24.2375 | 0 | 0 | 0 | 140.5775 | 843.465 | DE22 | A
DE | DE22C | DEAG_BYLA-K0113 | DETP_BYLA-K0113 | Moosthenning | 48.6666 | 12.4931 | 6000 | 5146 | NO | 32.1625 | 0 | 0 | 0 | 186.5425 | 1119.255 | DE22 | C
DE | DE22C | DEAG_BYLA-K0115 | DETP_BYLA-K0115 | Simbach | 48.5699 | 12.7439 | 6000 | 3137 | NO | 19.6062 | 0 | 0 | 0 | 113.7162 | 682.2975 | DE22 | A
DE | DE22C | DEAG_BYLA-K0119 | DETP_BYLA-K0119 | Eichendorf | 48.6358 | 12.8663 | 8000 | 5605 | NO | 35.0312 | 0 | 0 | 0 | 203.1812 | 1219.0875 | DE22 | B
DE | DE22C | DEAG_BYLA-K0120 | DETP_BYLA-K0120 | Mengkofen-Hüttenkofen | 48.7485 | 12.4727 | 12000 | 4414 | NO | 27.5875 | 0 | 0 | 0 | 160.0075 | 960.045 | DE22 | C
DE | DE22C | DEAG_BYLA-K0121 | DETP_BYLA-K0121 | Wallersdorf | 48.7381 | 12.7569 | 7000 | 5242 | NO | 32.7625 | 0 | 0 | 0 | 190.0225 | 1140.135 | DE22 | A
DE | DE22C | DEAG_BYLA-K0122 | DETP_BYLA-K0122 | AZV Mittlere Vils | 48.5793 | 12.6268 | 25000 | 17330 | NO | 108.3125 | 0 | 0 | 0 | 628.2125 | 3769.275 | DE22 | B
DE | DE22C | DEAG_BYLA-K0123 | DETP_BYLA-K0123 | Dingolfing | 48.6372 | 12.5182 | 70000 | 73042 | YES | 456.5125 | 1460.84 | 1095.63 | 2191.26 | 2647.7725 | 15886.635 | DE22 | B
DE | DE21B | DEAG_BYM-K0001 | DETP_BYM-K0001 | München II - Gut Marienhof | 48.292 | 11.6886 | 1000000 | 741000 | YES | 4631.25 | 14820 | 11115 | 22230 | 26861.25 | 161167.5 | DE21 | B
DE | DE212 | DEAG_BYM-K0002 | DETP_BYM-K0002 | München I | 48.2088 | 11.6294 | 1950000 | 980539 | YES | 6128.3688 | 19610.78 | 14708.085 | 29416.17 | 35544.5387 | 213267.2325 | DE21 | A
DE | DE21H | DEAG_BYM-K0018 | DETP_BYM-K0018 | Oberschleißheim | 48.2606 | 11.5417 | 30000 | 15016 | NO | 93.85 | 0 | 0 | 0 | 544.33 | 3265.98 | DE21 | B
DE | DE21H | DEAG_BYM-K0019 | DETP_BYM-K0019 | Ismaning | 48.2369 | 11.673 | 38000 | 26066 | NO | 162.9125 | 0 | 0 | 0 | 944.8925 | 5669.355 | DE21 | A
DE | DE21H | DEAG_BYM-K0023 | DETP_BYM-K0023 | Unterföhring | 48.2001 | 11.6617 | 20000 | 19584 | NO | 122.4 | 0 | 0 | 0 | 709.92 | 4259.52 | DE21 | A
DE | DE21H | DEAG_BYM-K0024 | DETP_BYM-K0024 | Schäftlarn | 47.9813 | 11.47 | 6960 | 5822 | NO | 36.3875 | 0 | 0 | 0 | 211.0475 | 1266.285 | DE21 | C
DE | DE21H | DEAG_BYM-K0025 | DETP_BYM-K0025 | Garching bei München | 48.269 | 11.6823 | 45000 | 33505 | NO | 209.4062 | 0 | 0 | 0 | 1214.5563 | 7287.3375 | DE21 | A
DE | DE217 | DEAG_BYM-K0031 | DETP_BYM-K0031 | Dachau | 48.2805 | 11.4694 | 95000 | 55411 | YES | 346.3187 | 1108.22 | 831.165 | 1662.33 | 2008.6487 | 12051.8925 | DE21 | B
DE | DE217 | DEAG_BYM-K00336 | DETP_BYM-K00336 | Sulzemoos | 48.2991 | 11.2741 | 6000 | 2020 | NOT KNOWN | 12.625 | 0 | 0 | 0 | 73.225 | 439.35 | DE21 | C
DE | DE217 | DEAG_BYM-K0040 | DETP_BYM-K0040 | Altomünster | 48.3588 | 11.2665 | 14000 | 13509 | NO | 84.4313 | 0 | 0 | 0 | 489.7013 | 2938.2075 | DE21 | C
DE | DE217 | DEAG_BYM-K0048 | DETP_BYM-K0048 | Erdweg | 48.3357 | 11.3046 | 8000 | 6564 | NO | 41.025 | 0 | 0 | 0 | 237.945 | 1427.67 | DE21 | B
DE | DE217 | DEAG_BYM-K0049 | DETP_BYM-K0049 | Odelzhausen | 48.3188 | 11.2195 | 12000 | 8856 | NO | 55.35 | 0 | 0 | 0 | 321.03 | 1926.18 | DE21 | C
DE | DE217 | DEAG_BYM-K0050 | DETP_BYM-K0050 | Haimhausen | 48.3192 | 11.5491 | 8800 | 5661 | NO | 35.3813 | 0 | 0 | 0 | 205.2112 | 1231.2675 | DE21 | A
DE | DE217 | DEAG_BYM-K0052 | DETP_BYM-K0052 | Petershausen | 48.4094 | 11.4799 | 9500 | 6727 | NO | 42.0438 | 0 | 0 | 0 | 243.8537 | 1463.1225 | DE21 | B
DE | DE217 | DEAG_BYM-K0065 | DETP_BYM-K0065 | Markt Indersdorf | 48.3633 | 11.3834 | 18000 | 11947 | NO | 74.6688 | 0 | 0 | 0 | 433.0787 | 2598.4725 | DE21 | B
DE | DE217 | DEAG_BYM-K0067 | DETP_BYM-K0067 | Hebertshausen | 48.303 | 11.4998 | 10000 | 6259 | NO | 39.1187 | 0 | 0 | 0 | 226.8887 | 1361.3325 | DE21 | B
DE | DE217 | DEAG_BYM-K0068 | DETP_BYM-K0068 | Vierkirchen | 48.3828 | 11.4538 | 7500 | 4693 | NO | 29.3313 | 0 | 0 | 0 | 170.1212 | 1020.7275 | DE21 | C
DE | DE217 | DEAG_BYM-K0069 | DETP_BYM-K0069 | Karlsfeld | 48.2476 | 11.4802 | 45000 | 34367 | YES | 214.7938 | 687.34 | 515.505 | 1031.01 | 1245.8038 | 7474.8225 | DE21 | C
DE | DE21A | DEAG_BYM-K0070 | DETP_BYM-K0070 | Dorfen | 48.2745 | 12.1631 | 15000 | 19413 | NO | 121.3313 | 0 | 0 | 0 | 703.7212 | 4222.3275 | DE21 | B
DE | DE21A | DEAG_BYM-K0073 | DETP_BYM-K0073 | Isen | 48.2206 | 12.0514 | 6200 | 4542 | NO | 28.3875 | 0 | 0 | 0 | 164.6475 | 987.885 | DE21 | A
DE | DE21A | DEAG_BYM-K0074 | DETP_BYM-K0074 | Taufkirchen / Vils | 48.3424 | 12.1397 | 17000 | 15407 | NO | 96.2938 | 0 | 0 | 0 | 558.5037 | 3351.0225 | DE21 | A
DE | DE21A | DEAG_BYM-K0080 | DETP_BYM-K0080 | Wartenberg | 48.4156 | 11.9818 | 6000 | 10900 | NO | 68.125 | 0 | 0 | 0 | 395.125 | 2370.75 | DE21 | B
DE | DE21A | DEAG_BYM-K0083 | DETP_BYM-K0083 | AZV Erdinger Moos | 48.3733 | 11.8933 | 320000 | 172383 | YES | 1077.3937 | 3447.66 | 2585.745 | 5171.49 | 6248.8837 | 37493.3025 | DE21 | A
DE | DE21A | DEAG_BYM-K0088 | DETP_BYM-K0088 | Sankt Wolfgang | 48.2253 | 12.1373 | 6000 | 3600 | NO | 22.5 | 0 | 0 | 0 | 130.5 | 783 | DE21 | B
DE | DE21A | DEAG_BYM-K0089 | DETP_BYM-K0089 | gku VE München-Ost | 48.2252 | 11.8181 | 135000 | 129828 | YES | 811.425 | 2596.56 | 1947.42 | 3894.84 | 4706.265 | 28237.59 | DE21 | A
DE | DE21B | DEAG_BYM-K0097 | DETP_BYM-K0097 | Moosburg | 48.4889 | 11.9478 | 50000 | 29643 | YES | 185.2687 | 592.86 | 444.645 | 889.29 | 1074.5587 | 6447.3525 | DE21 | B
DE | DE21B | DEAG_BYM-K0107 | DETP_BYM-K0107 | Fahrenzhausen | 48.3648 | 11.581 | 6000 | 5500 | NO | 34.375 | 0 | 0 | 0 | 199.375 | 1196.25 | DE21 | A
DE | DE21B | DEAG_BYM-K0108 | DETP_BYM-K0108 | ZV Unterschleißheim, Eching u. Neufahrn | 48.3244 | 11.6978 | 160000 | 71130 | YES | 444.5625 | 1422.6 | 1066.95 | 2133.9 | 2578.4625 | 15470.775 | DE21 | B
DE | DE21B | DEAG_BYM-K0109 | DETP_BYM-K0109 | Hallbergmoos | 48.3344 | 11.7477 | 15000 | 12133 | NO | 75.8312 | 0 | 0 | 0 | 439.8212 | 2638.9275 | DE21 | A
DE | DE21B | DEAG_BYM-K0110 | DETP_BYM-K0110 | Hohenkammer | 48.4296 | 11.5607 | 6000 | 3163 | NO | 19.7688 | 0 | 0 | 0 | 114.6587 | 687.9525 | DE21 | C
DE | DE21B | DEAG_BYM-K0111 | DETP_BYM-K0111 | Freising | 48.4046 | 11.7608 | 110000 | 66790 | YES | 417.4375 | 1335.8 | 1001.85 | 2003.7 | 2421.1375 | 14526.825 | DE21 | A
DE | DE21B | DEAG_BYM-K0114 | DETP_BYM-K0114 | Zolling | 48.445 | 11.7869 | 8000 | 5987 | NO | 37.4188 | 0 | 0 | 0 | 217.0288 | 1302.1725 | DE21 | C
DE | DE21B | DEAG_BYM-K0115 | DETP_BYM-K0115 | Au i.d. Hallertau | 48.5664 | 11.7419 | 12000 | 10371 | NO | 64.8188 | 0 | 0 | 0 | 375.9488 | 2255.6925 | DE21 | B
DE | DE21B | DEAG_BYM-K0116 | DETP_BYM-K0116 | Allershausen | 48.4374 | 11.6055 | 12000 | 6708 | NO | 41.925 | 0 | 0 | 0 | 243.165 | 1458.99 | DE21 | B
DE | DE21C | DEAG_BYM-K0121 | DETP_BYM-K0121 | Amperverband | 48.2338 | 11.3605 | 240000 | 169079 | YES | 1056.7438 | 3381.58 | 2536.185 | 5072.37 | 6129.1138 | 36774.6825 | DE21 | B
DE | DE21C | DEAG_BYM-K0123 | DETP_BYM-K0123 | ZV Obere Amper | 48.124 | 11.1778 | 13000 | 9517 | NO | 59.4812 | 0 | 0 | 0 | 344.9912 | 2069.9475 | DE21 | B
DE | DE21C | DEAG_BYM-K0126 | DETP_BYM-K0126 | ZV Schweinbach-Glonngruppe | 48.2761 | 11.1664 | 6500 | 5110 | NO | 31.9375 | 0 | 0 | 0 | 185.2375 | 1111.425 | DE21 | B
DE | DE21C | DEAG_BYM-K0127 | DETP_BYM-K0127 | AZV Obere Maisach | 48.1926 | 11.1088 | 7000 | 5949 | NO | 37.1812 | 0 | 0 | 0 | 215.6512 | 1293.9075 | DE21 | C
DE | DE21C | DEAG_BYM-K0128 | DETP_BYM-K0128 | Mammendorf | 48.2171 | 11.1806 | 10000 | 5783 | NO | 36.1438 | 0 | 0 | 0 | 209.6338 | 1257.8025 | DE21 | A
DE | DE21C | DEAG_BYM-K0130 | DETP_BYM-K0130 | Fürstenfeldbruck | 48.186 | 11.303 | 100000 | 48388 | YES | 302.425 | 967.76 | 725.82 | 1451.64 | 1754.065 | 10524.39 | DE21 | A
DE | DE252 | DEAG_BYN-K0002 | DETP_BYN-K0002 | Erlangen | 49.6171 | 11.0009 | 350000 | 252000 | YES | 1575 | 5040 | 3780 | 7560 | 9135 | 54810 | DE25 | B
DE | DE253 | DEAG_BYN-K0003 | DETP_BYN-K0003 | Fürth | 49.4907 | 10.9875 | 265000 | 190800 | YES | 1192.5 | 3816 | 2862 | 5724 | 6916.5 | 41499 | DE25 | A
DE | DE253 | DEAG_BYN-K0004 | DETP_BYN-K0004 | Fürth OT Stadeln-Vach | 49.5337 | 10.9713 | 26000 | 17680 | NO | 110.5 | 0 | 0 | 0 | 640.9 | 3845.4 | DE25 | A
DE | DE254 | DEAG_BYN-K0005 | DETP_BYN-K0005 | Nürnberg I | 49.4654 | 11.0204 | 1400000 | 1008000 | YES | 6300 | 20160 | 15120 | 30240 | 36540 | 219240 | DE25 | A
DE | DE254 | DEAG_BYN-K0006 | DETP_BYN-K0006 | Nürnberg II | 49.4597 | 11.0433 | 230000 | 165600 | YES | 1035 | 3312 | 2484 | 4968 | 6003 | 36018 | DE25 | A
DE | DE255 | DEAG_BYN-K0008 | DETP_BYN-K0008 | Schwabach | 49.338 | 11.0587 | 95000 | 64600 | YES | 403.75 | 1292 | 969 | 1938 | 2341.75 | 14050.5 | DE25 | B
DE | DE257 | DEAG_BYN-K0014 | DETP_BYN-K0014 | Röttenbach | 49.654 | 10.9225 | 11000 | 9022 | NO | 56.3875 | 0 | 0 | 0 | 327.0475 | 1962.285 | DE25 | B
DE | DE257 | DEAG_BYN-K0016 | DETP_BYN-K0016 | KA Wachenroth | 49.7505 | 10.726 | 6000 | 3249 | NO | 20.3063 | 0 | 0 | 0 | 117.7763 | 706.6575 | DE25 | B
DE | DE257 | DEAG_BYN-K0020 | DETP_BYN-K0020 | KA Adelsdorf | 49.7182 | 10.9097 | 25000 | 18486 | NO | 115.5375 | 0 | 0 | 0 | 670.1175 | 4020.705 | DE25 | B
DE | DE257 | DEAG_BYN-K0026 | DETP_BYN-K0026 | Heroldsberg | 49.524 | 11.1434 | 12000 | 10574 | NO | 66.0875 | 0 | 0 | 0 | 383.3075 | 2299.845 | DE25 | A
DE | DE257 | DEAG_BYN-K0027 | DETP_BYN-K0027 | Vestenbergsgreuth | 49.6915 | 10.6666 | 5500 | 2025 | NO | 12.6562 | 0 | 0 | 0 | 73.4062 | 440.4375 | DE25 | C
DE | DE257 | DEAG_BYN-K0028 | DETP_BYN-K0028 | Herzogenaurach | 49.562 | 10.9338 | 65000 | 33988 | YES | 212.425 | 679.76 | 509.82 | 1019.64 | 1232.065 | 7392.39 | DE25 | C
DE | DE257 | DEAG_BYN-K0030 | DETP_BYN-K0030 | Höchstadt a.d.Aisch | 49.7068 | 10.8455 | 35000 | 23046 | NO | 144.0375 | 0 | 0 | 0 | 835.4175 | 5012.505 | DE25 | B
DE | DE257 | DEAG_BYN-K0031 | DETP_BYN-K0031 | AGV Mittlere Regnitz | 49.6741 | 11.0452 | 25000 | 19301 | NO | 120.6313 | 0 | 0 | 0 | 699.6613 | 4197.9675 | DE25 | B
DE | DE258 | DEAG_BYN-K0032 | DETP_BYN-K0032 | Roßtal | 49.4022 | 10.8949 | 8000 | 6317 | NO | 39.4813 | 0 | 0 | 0 | 228.9913 | 1373.9475 | DE25 | B
DE | DE258 | DEAG_BYN-K0035 | DETP_BYN-K0035 | KA Veitsbronn | 49.5061 | 10.9078 | 12000 | 8904 | NO | 55.65 | 0 | 0 | 0 | 322.77 | 1936.62 | DE25 | C
DE | DE258 | DEAG_BYN-K0048 | DETP_BYN-K0048 | KA Langenzenn | 49.4993 | 10.8099 | 20000 | 15038 | NO | 93.9875 | 0 | 0 | 0 | 545.1275 | 3270.765 | DE25 | A
DE | DE258 | DEAG_BYN-K0050 | DETP_BYN-K0050 | ZV Oberes Zenntal S. Wilhermsdorf | 49.4837 | 10.7302 | 14000 | 9520 | NO | 59.5 | 0 | 0 | 0 | 345.1 | 2070.6 | DE25 | B
DE | DE259 | DEAG_BYN-K0066 | DETP_BYN-K0066 | Röthenbach/Pegnitz | 49.4841 | 11.2282 | 30000 | 20400 | NO | 127.5 | 0 | 0 | 0 | 739.5 | 4437 | DE25 | A
DE | DE259 | DEAG_BYN-K0072 | DETP_BYN-K0072 | Feucht | 49.3704 | 11.1994 | 28000 | 19040 | NO | 119 | 0 | 0 | 0 | 690.2 | 4141.2 | DE25 | B
DE | DE259 | DEAG_BYN-K0073 | DETP_BYN-K0073 | Winkelhaid | 49.3839 | 11.2826 | 5000 | 3450 | NO | 21.5625 | 0 | 0 | 0 | 125.0625 | 750.375 | DE25 | C
DE | DE259 | DEAG_BYN-K0090 | DETP_BYN-K0090 | Neuhaus/Pegnitz | 49.6258 | 11.548 | 5700 | 3705 | NOT KNOWN | 23.1562 | 0 | 0 | 0 | 134.3062 | 805.8375 | DE25 | A
DE | DE259 | DEAG_BYN-K0095 | DETP_BYN-K0095 | Leinburg | 49.4545 | 11.2749 | 12000 | 8160 | NO | 51 | 0 | 0 | 0 | 295.8 | 1774.8 | DE25 | A
DE | DE259 | DEAG_BYN-K0096 | DETP_BYN-K0096 | Altdorf/Nürnberg | 49.3687 | 11.3945 | 20000 | 13600 | NO | 85 | 0 | 0 | 0 | 493 | 2958 | DE25 | C
DE | DE259 | DEAG_BYN-K0097 | DETP_BYN-K0097 | Hersbruck | 49.5052 | 11.4029 | 36000 | 24480 | NO | 153 | 0 | 0 | 0 | 887.4 | 5324.4 | DE25 | B
DE | DE259 | DEAG_BYN-K0098 | DETP_BYN-K0098 | ZV Schwarzachgruppe Sitz Schwarzenbruck | 49.3519 | 11.2221 | 33000 | 22440 | NO | 140.25 | 0 | 0 | 0 | 813.45 | 4880.7 | DE25 | A
DE | DE259 | DEAG_BYN-K0099 | DETP_BYN-K0099 | Lauf/Pegnitz | 49.5051 | 11.273 | 49000 | 33320 | YES | 208.25 | 666.4 | 499.8 | 999.6 | 1207.85 | 7247.1 | DE25 | A
DE | DE259 | DEAG_BYN-K0104 | DETP_BYN-K0104 | ZV Schnaittachtal | 49.5187 | 11.3262 | 45000 | 30600 | NO | 191.25 | 0 | 0 | 0 | 1109.25 | 6655.5 | DE25 | A
DE | DE25B | DEAG_BYN-K0106 | DETP_BYN-K0106 | Büchenbach | 49.2702 | 11.075 | 5000 | 2626 | NO | 16.4125 | 0 | 0 | 0 | 95.1925 | 571.155 | DE25 | B
DE | DE25B | DEAG_BYN-K0113 | DETP_BYN-K0113 | Greding | 49.0361 | 11.3633 | 8000 | 6556 | NO | 40.975 | 0 | 0 | 0 | 237.655 | 1425.93 | DE25 | B
DE | DE25B | DEAG_BYN-K0117 | DETP_BYN-K0117 | Georgensgmünd | 49.1952 | 11.0299 | 20000 | 9941 | NO | 62.1313 | 0 | 0 | 0 | 360.3612 | 2162.1675 | DE25 | B
DE | DE25B | DEAG_BYN-K0125 | DETP_BYN-K0125 | Rednitzhembach | 49.3069 | 11.0732 | 8000 | 6684 | NO | 41.775 | 0 | 0 | 0 | 242.295 | 1453.77 | DE25 | A
DE | DE25B | DEAG_BYN-K0148 | DETP_BYN-K0148 | Heideck | 49.1423 | 11.1556 | 12000 | 7967 | NO | 49.7937 | 0 | 0 | 0 | 288.8037 | 1732.8225 | DE25 | B
DE | DE25B | DEAG_BYN-K0149 | DETP_BYN-K0149 | Abenberg | 49.2393 | 10.9762 | 8000 | 5130 | NO | 32.0625 | 0 | 0 | 0 | 185.9625 | 1115.775 | DE25 | B
DE | DE25B | DEAG_BYN-K0154 | DETP_BYN-K0154 | Hilpoltstein | 49.1899 | 11.1583 | 25000 | 16589 | NO | 103.6812 | 0 | 0 | 0 | 601.3512 | 3608.1075 | DE25 | C
DE | DE25B | DEAG_BYN-K0173 | DETP_BYN-K0173 | Spalt | 49.1778 | 10.9355 | 12000 | 11987 | NO | 74.9188 | 0 | 0 | 0 | 434.5288 | 2607.1725 | DE25 | B
DE | DE25B | DEAG_BYN-K0177 | DETP_BYN-K0177 | Thalmässing | 49.0876 | 11.2401 | 5300 | 4133 | NO | 25.8313 | 0 | 0 | 0 | 149.8212 | 898.9275 | DE25 | C
DE | DE25B | DEAG_BYN-K0179 | DETP_BYN-K0179 | ZV Unteres Schwarzachtal S.Wendelstein | 49.3417 | 11.1068 | 40000 | 32571 | YES | 203.5688 | 651.42 | 488.565 | 977.13 | 1180.6988 | 7084.1925 | DE25 | A
DE | DE25B | DEAG_BYN-K0180 | DETP_BYN-K0180 | KA Roth Stadt | 49.2523 | 11.081 | 65000 | 36000 | YES | 225 | 720 | 540 | 1080 | 1305 | 7830 | DE25 | B
DE | DE238 | DEAG_BYR-K0001 | DETP_BYR-K0001 | Regensburg | 49.0062 | 12.1846 | 400000 | 288824 | YES | 1805.15 | 5776.48 | 4332.36 | 8664.72 | 10469.87 | 62819.22 | DE23 | A
DE | DE235 | DEAG_BYR-K0003 | DETP_BYR-K0003 | Furth im Wald | 49.3024 | 12.8345 | 25000 | 18333 | NO | 114.5813 | 0 | 0 | 0 | 664.5713 | 3987.4275 | DE23 | A
DE | DE235 | DEAG_BYR-K0005 | DETP_BYR-K0005 | Waldmünchen | 49.3811 | 12.6906 | 13000 | 9454 | NO | 59.0875 | 0 | 0 | 0 | 342.7075 | 2056.245 | DE23 | A
DE | DE235 | DEAG_BYR-K0016 | DETP_BYR-K0016 | Zandt | 49.1438 | 12.7436 | 5000 | 2076 | NO | 12.975 | 0 | 0 | 0 | 75.255 | 451.53 | DE23 | C
DE | DE235 | DEAG_BYR-K0019 | DETP_BYR-K0019 | Rötz | 49.3393 | 12.5159 | 9000 | 3269 | NO | 20.4313 | 0 | 0 | 0 | 118.5012 | 711.0075 | DE23 | B
DE | DE235 | DEAG_BYR-K0057 | DETP_BYR-K0057 | Bad Kötzting | 49.1671 | 12.835 | 20000 | 12916 | NO | 80.725 | 0 | 0 | 0 | 468.205 | 2809.23 | DE23 | C
DE | DE235 | DEAG_BYR-K0060 | DETP_BYR-K0060 | ZV Lamer Winkel | 49.2022 | 12.9886 | 21500 | 11060 | NO | 69.125 | 0 | 0 | 0 | 400.925 | 2405.55 | DE23 | B
DE | DE235 | DEAG_BYR-K0061 | DETP_BYR-K0061 | Cham | 49.224 | 12.6451 | 38200 | 51554 | YES | 322.2125 | 1031.08 | 773.31 | 1546.62 | 1868.8325 | 11212.995 | DE23 | A
DE | DE235 | DEAG_BYR-K0062 | DETP_BYR-K0062 | Roding | 49.1929 | 12.5007 | 25000 | 11056 | NO | 69.1 | 0 | 0 | 0 | 400.78 | 2404.68 | DE23 | B
DE | DE236 | DEAG_BYR-K0069 | DETP_BYR-K0069 | Mühlhausen | 49.1639 | 11.45 | 6700 | 7173 | NO | 44.8313 | 0 | 0 | 0 | 260.0213 | 1560.1275 | DE23 | A
DE | DE236 | DEAG_BYR-K0074 | DETP_BYR-K0074 | Hohenfels-Milit. Einrichtung | 49.2178 | 11.8404 | 12000 | 2555 | NO | 15.9688 | 0 | 0 | 0 | 92.6188 | 555.7125 | DE23 | A
DE | DE236 | DEAG_BYR-K0078 | DETP_BYR-K0078 | Postbauer-Heng | 49.2927 | 11.3376 | 10000 | 9703 | NO | 60.6438 | 0 | 0 | 0 | 351.7337 | 2110.4025 | DE23 | B
DE | DE236 | DEAG_BYR-K0082 | DETP_BYR-K0082 | Berching | 49.0939 | 11.4458 | 12000 | 5247 | NO | 32.7938 | 0 | 0 | 0 | 190.2038 | 1141.2225 | DE23 | A
DE | DE236 | DEAG_BYR-K0091 | DETP_BYR-K0091 | Berg | 49.3474 | 11.4373 | 10000 | 7166 | NO | 44.7875 | 0 | 0 | 0 | 259.7675 | 1558.605 | DE23 | B
DE | DE236 | DEAG_BYR-K0092 | DETP_BYR-K0092 | Parsberg | 49.17 | 11.7304 | 13300 | 10969 | NO | 68.5563 | 0 | 0 | 0 | 397.6263 | 2385.7575 | DE23 | A
DE | DE236 | DEAG_BYR-K0096 | DETP_BYR-K0096 | Velburg | 49.1979 | 11.6599 | 11000 | 6571 | NO | 41.0688 | 0 | 0 | 0 | 238.1987 | 1429.1925 | DE23 | C
DE | DE236 | DEAG_BYR-K0098 | DETP_BYR-K0098 | Neumarkt/Opf. | 49.301 | 11.4673 | 150000 | 107802 | YES | 673.7625 | 2156.04 | 1617.03 | 3234.06 | 3907.8225 | 23446.935 | DE23 | A
DE | DE236 | DEAG_BYR-K0101 | DETP_BYR-K0101 | Freystadt | 49.1917 | 11.3332 | 8000 | 6302 | NO | 39.3875 | 0 | 0 | 0 | 228.4475 | 1370.685 | DE23 | B
DE | DE236 | DEAG_BYR-K0102 | DETP_BYR-K0102 | Dietfurt | 49.0215 | 11.5927 | 6500 | 5832 | NO | 36.45 | 0 | 0 | 0 | 211.41 | 1268.46 | DE23 | B
DE | DE238 | DEAG_BYR-K0106 | DETP_BYR-K0106 | Schierling | 48.8357 | 12.1514 | 16200 | 12394 | NO | 77.4625 | 0 | 0 | 0 | 449.2825 | 2695.695 | DE23 | B
DE | DE238 | DEAG_BYR-K0108 | DETP_BYR-K0108 | Beratzhausen | 49.0931 | 11.8154 | 6500 | 4278 | NO | 26.7375 | 0 | 0 | 0 | 155.0775 | 930.465 | DE23 | A
DE | DE238 | DEAG_BYR-K0112 | DETP_BYR-K0112 | Bernhardswald | 49.0922 | 12.226 | 6300 | 2414 | NO | 15.0875 | 0 | 0 | 0 | 87.5075 | 525.045 | DE23 | C
DE | DE238 | DEAG_BYR-K0113 | DETP_BYR-K0113 | Pfatter | 48.9714 | 12.3951 | 6000 | 2641 | NOT KNOWN | 16.5063 | 0 | 0 | 0 | 95.7362 | 574.4175 | DE23 | B
DE | DE238 | DEAG_BYR-K0118 | DETP_BYR-K0118 | Nittendorf OT Etterzhausen | 49.0255 | 11.9882 | 6300 | 2246 | NO | 14.0375 | 0 | 0 | 0 | 81.4175 | 488.505 | DE23 | B
DE | DE238 | DEAG_BYR-K0119 | DETP_BYR-K0119 | ZV Pfattertal Sitz Mintraching | 48.9443 | 12.241 | 18000 | 13648 | NO | 85.3 | 0 | 0 | 0 | 494.74 | 2968.44 | DE23 | B
DE | DE238 | DEAG_BYR-K0121 | DETP_BYR-K0121 | Sinzing | 48.9998 | 12.0337 | 6000 | 2529 | NOT KNOWN | 15.8063 | 0 | 0 | 0 | 91.6762 | 550.0575 | DE23 | A
DE | DE238 | DEAG_BYR-K0122 | DETP_BYR-K0122 | ZV Wörth a.d. Donau Sitz Wörth | 48.9941 | 12.4071 | 9800 | 9578 | NO | 59.8625 | 0 | 0 | 0 | 347.2025 | 2083.215 | DE23 | A
DE | DE238 | DEAG_BYR-K0129 | DETP_BYR-K0129 | Laaber | 49.0648 | 11.9011 | 7500 | 4983 | NO | 31.1438 | 0 | 0 | 0 | 180.6338 | 1083.8025 | DE23 | C
DE | DE238 | DEAG_BYR-K0131 | DETP_BYR-K0131 | Sinzing OT Eilsbrunn | 49.0024 | 11.9663 | 5800 | 2369 | NOT KNOWN | 14.8063 | 0 | 0 | 0 | 85.8762 | 515.2575 | DE23 | B
DE | DE238 | DEAG_BYR-K0133 | DETP_BYR-K0133 | ZV Labertal Sitz Nittendorf | 49.0246 | 11.9253 | 9000 | 8697 | NO | 54.3562 | 0 | 0 | 0 | 315.2662 | 1891.5975 | DE23 | A
DE | DE238 | DEAG_BYR-K0137 | DETP_BYR-K0137 | Hemau | 49.0694 | 11.8239 | 16000 | 5138 | NO | 32.1125 | 0 | 0 | 0 | 186.2525 | 1117.515 | DE23 | C
DE | DE213 | DEAG_BYRO-K0001 | DETP_BYRO-K0001 | Rosenheim | 47.8762 | 12.1299 | 350000 | 112887 | YES | 705.5437 | 2257.74 | 1693.305 | 3386.61 | 4092.1537 | 24552.9225 | DE21 | A
DE | DE21F | DEAG_BYRO-K0003 | DETP_BYRO-K0003 | Holzkirchen Fellach | 47.9083 | 11.7425 | 50000 | 34000 | YES | 212.5 | 680 | 510 | 1020 | 1232.5 | 7395 | DE21 | C
DE | DE21F | DEAG_BYRO-K0009 | DETP_BYRO-K0009 | Valley | 47.8932 | 11.7753 | 5000 | 3450 | NO | 21.5625 | 0 | 0 | 0 | 125.0625 | 750.375 | DE21 | B
DE | DE21F | DEAG_BYRO-K0011 | DETP_BYRO-K0011 | ZV Tegernsee Sitz Gmund a.T. | 47.7647 | 11.7578 | 60000 | 59553 | YES | 372.2063 | 1191.06 | 893.295 | 1786.59 | 2158.7962 | 12952.7775 | DE21 | C
DE | DE21F | DEAG_BYRO-K0012 | DETP_BYRO-K0012 | Irschenberg | 47.841 | 11.9215 | 5000 | 3450 | NO | 21.5625 | 0 | 0 | 0 | 125.0625 | 750.375 | DE21 | C
DE | DE21F | DEAG_BYRO-K0013 | DETP_BYRO-K0013 | ZV Schlierachtal Sitz Miesbach | 47.803 | 11.825 | 80000 | 32165 | YES | 201.0312 | 643.3 | 482.475 | 964.95 | 1165.9813 | 6995.8875 | DE21 | A
DE | DE21F | DEAG_BYRO-K0015 | DETP_BYRO-K0015 | Fischbachau OT Wörnsmühl | 47.7739 | 11.9004 | 12000 | 8160 | NO | 51 | 0 | 0 | 0 | 295.8 | 1774.8 | DE21 | C
DE | DE21G | DEAG_BYRO-K0025 | DETP_BYRO-K0025 | Neumarkt-St.Veit | 48.3659 | 12.5215 | 15000 | 8183 | NO | 51.1438 | 0 | 0 | 0 | 296.6338 | 1779.8025 | DE21 | B
DE | DE21G | DEAG_BYRO-K0039 | DETP_BYRO-K0039 | Haag/Ob | 48.146 | 12.199 | 30000 | 46919 | NO | 293.2438 | 0 | 0 | 0 | 1700.8138 | 10204.8825 | DE21 | C
DE | DE21G | DEAG_BYRO-K0044 | DETP_BYRO-K0044 | Waldkraiburg | 48.2026 | 12.421 | 64500 | 45524 | YES | 284.525 | 910.48 | 682.86 | 1365.72 | 1650.245 | 9901.47 | DE21 | A
DE | DE21G | DEAG_BYRO-K0045 | DETP_BYRO-K0045 | Gars/Inn | 48.1529 | 12.2835 | 5600 | 6250 | NO | 39.0625 | 0 | 0 | 0 | 226.5625 | 1359.375 | DE21 | B
DE | DE21G | DEAG_BYRO-K0046 | DETP_BYRO-K0046 | Mühldorf a.Inn | 48.2374 | 12.5442 | 30000 | 24997 | NO | 156.2313 | 0 | 0 | 0 | 906.1413 | 5436.8475 | DE21 | A
DE | DE21G | DEAG_BYRO-K0052 | DETP_BYRO-K0052 | Ampfing | 48.2605 | 12.4294 | 24000 | 15905 | NO | 99.4062 | 0 | 0 | 0 | 576.5562 | 3459.3375 | DE21 | A
DE | DE21K | DEAG_BYRO-K0054 | DETP_BYRO-K0054 | Kiefersfelden | 47.607 | 12.1994 | 20000 | 10125 | NO | 63.2812 | 0 | 0 | 0 | 367.0312 | 2202.1875 | DE21 | A
DE | DE21K | DEAG_BYRO-K0059 | DETP_BYRO-K0059 | Halfing | 47.9474 | 12.2673 | 5000 | 4166 | NO | 26.0375 | 0 | 0 | 0 | 151.0175 | 906.105 | DE21 | B
DE | DE21K | DEAG_BYRO-K0062 | DETP_BYRO-K0062 | Bad Feilnbach | 47.7957 | 12.0159 | 20000 | 11029 | NO | 68.9313 | 0 | 0 | 0 | 399.8012 | 2398.8075 | DE21 | C
DE | DE21K | DEAG_BYRO-K0065 | DETP_BYRO-K0065 | Bad Aibling | 47.8499 | 12.0259 | 36000 | 64660 | NO | 404.125 | 0 | 0 | 0 | 2343.925 | 14063.55 | DE21 | B
DE | DE21K | DEAG_BYRO-K0071 | DETP_BYRO-K0071 | Feldkirchen-Westerham | 47.8922 | 11.8648 | 20000 | 12632 | NO | 78.95 | 0 | 0 | 0 | 457.91 | 2747.46 | DE21 | B
DE | DE21K | DEAG_BYRO-K0082 | DETP_BYRO-K0082 | Oberaudorf | 47.6726 | 12.1732 | 15500 | 5440 | NO | 34 | 0 | 0 | 0 | 197.2 | 1183.2 | DE21 | B
DE | DE21K | DEAG_BYRO-K0085 | DETP_BYRO-K0085 | Eggstätt | 47.9302 | 12.3914 | 6500 | 2368 | NO | 14.8 | 0 | 0 | 0 | 85.84 | 515.04 | DE21 | A
DE | DE21K | DEAG_BYRO-K0102 | DETP_BYRO-K0102 | Raubling | 47.8112 | 12.1254 | 33700 | 10733 | NO | 67.0812 | 0 | 0 | 0 | 389.0712 | 2334.4275 | DE21 | B
DE | DE21K | DEAG_BYRO-K0104 | DETP_BYRO-K0104 | ZV Simssee-Prien-Achental | 47.8398 | 12.1569 | 65000 | 43040 | YES | 269 | 860.8 | 645.6 | 1291.2 | 1560.2 | 9361.2 | DE21 | B
DE | DE21K | DEAG_BYRO-K0108 | DETP_BYRO-K0108 | Wasserburg/Inn | 48.0712 | 12.2181 | 50000 | 59163 | YES | 369.7688 | 1183.26 | 887.445 | 1774.89 | 2144.6587 | 12867.9525 | DE21 | C
DE | DE21K | DEAG_BYRO-K0112 | DETP_BYRO-K0112 | ZV Brannenburg-Flintsbach | 47.7416 | 12.1204 | 29000 | 13171 | NO | 82.3188 | 0 | 0 | 0 | 477.4488 | 2864.6925 | DE21 | C
DE | DE21K | DEAG_BYRO-K0113 | DETP_BYRO-K0113 | Bruckmühl | 47.8668 | 11.9702 | 25000 | 18163 | NO | 113.5188 | 0 | 0 | 0 | 658.4087 | 3950.4525 | DE21 | A
DE | DE21K | DEAG_BYRO-K0116 | DETP_BYRO-K0116 | ZV Chiemsee | 47.8603 | 12.2833 | 85000 | 67966 | YES | 424.7875 | 1359.32 | 1019.49 | 2038.98 | 2463.7675 | 14782.605 | DE21 | C
DE | DE218 | DEAG_BYRO-K0126 | DETP_BYRO-K0126 | Ebersberg | 48.0785 | 11.9881 | 18100 | 7750 | NO | 48.4375 | 0 | 0 | 0 | 280.9375 | 1685.625 | DE21 | C
DE | DE218 | DEAG_BYRO-K0130 | DETP_BYRO-K0130 | Aßling | 47.9864 | 12.0112 | 8000 | 5941 | NO | 37.1313 | 0 | 0 | 0 | 215.3612 | 1292.1675 | DE21 | B
DE | DE218 | DEAG_BYRO-K0134 | DETP_BYRO-K0134 | Glonn | 47.9821 | 11.8726 | 7300 | 3627 | NO | 22.6687 | 0 | 0 | 0 | 131.4787 | 788.8725 | DE21 | B
DE | DE218 | DEAG_BYRO-K0137 | DETP_BYRO-K0137 | Grafing/München | 48.0374 | 11.9754 | 26000 | 14949 | NO | 93.4312 | 0 | 0 | 0 | 541.9012 | 3251.4075 | DE21 | B
DE | DE214 | DEAG_BYTS-K0001 | DETP_BYTS-K0001 | Altötting-Neuötting | 48.2556 | 12.7036 | 48500 | 41891 | YES | 261.8188 | 837.82 | 628.365 | 1256.73 | 1518.5487 | 9111.2925 | DE21 | C
DE | DE214 | DEAG_BYTS-K0003 | DETP_BYTS-K0003 | Burghausen | 48.1748 | 12.8479 | 30000 | 20400 | NO | 127.5 | 0 | 0 | 0 | 739.5 | 4437 | DE21 | A
DE | DE214 | DEAG_BYTS-K0006 | DETP_BYTS-K0006 | Garching/Alz | 48.1373 | 12.6153 | 18000 | 13226 | NO | 82.6625 | 0 | 0 | 0 | 479.4425 | 2876.655 | DE21 | B
DE | DE214 | DEAG_BYTS-K0007 | DETP_BYTS-K0007 | Marktl | 48.2472 | 12.8638 | 6000 | 3717 | NO | 23.2313 | 0 | 0 | 0 | 134.7413 | 808.4475 | DE21 | C
DE | DE214 | DEAG_BYTS-K0008 | DETP_BYTS-K0008 | Töging/Inn | 48.2477 | 12.6015 | 22000 | 24326 | NO | 152.0375 | 0 | 0 | 0 | 881.8175 | 5290.905 | DE21 | B
DE | DE40H | DEAG_BB418 | DETP_BB418 | Zossen Tandem-KA | 52.1975 | 13.4653 | 49666 | 35348 | YES | 220.925 | 706.96 | 530.22 | 1060.44 | 1281.365 | 7688.19 | DE40 | B
DE | DE40C | DEAG_BB44 | DETP_BB44 | Eisenhüttenstadt | 52.1222 | 14.6514 | 99000 | 40553 | YES | 253.4562 | 811.06 | 608.295 | 1216.59 | 1470.0462 | 8820.2775 | DE40 | B
DE | DE407 | DEAG_BB46 | DETP_BB46 | Elsterwerda | 51.4585 | 13.5401 | 80000 | 18816 | YES | 117.6 | 376.32 | 282.24 | 564.48 | 682.08 | 4092.48 | DE40 | A
DE | DE40D | DEAG_BB48 | DETP_BB48 | Fehrbellin | 52.8134 | 12.7406 | 15000 | 9286 | NO | 58.0375 | 0 | 0 | 0 | 336.6175 | 2019.705 | DE40 | C
DE | DE40I | DEAG_BB5 | DETP_BB5 | Angermünde | 53.0241 | 13.9784 | 16000 | 10321 | NO | 64.5063 | 0 | 0 | 0 | 374.1363 | 2244.8175 | DE40 | B
DE | DE407 | DEAG_BB50 | DETP_BB50 | Finsterwalde | 51.6186 | 13.7017 | 25000 | 17304 | NO | 108.15 | 0 | 0 | 0 | 627.27 | 3763.62 | DE40 | A
DE | DE40G | DEAG_BB52 | DETP_BB52 | Forst | 51.7611 | 14.6499 | 30000 | 17531 | NO | 109.5688 | 0 | 0 | 0 | 635.4987 | 3812.9925 | DE40 | B
DE | DE403 | DEAG_BB53 | DETP_BB53 | Frankfurt (Oder) | 52.3683 | 14.5475 | 120000 | 65038 | YES | 406.4875 | 1300.76 | 975.57 | 1951.14 | 2357.6275 | 14145.765 | DE40 | A
DE | DE407 | DEAG_BB6 | DETP_BB6 | Bad Liebenwerda | 51.5228 | 13.3892 | 20000 | 8606 | NO | 53.7875 | 0 | 0 | 0 | 311.9675 | 1871.805 | DE40 | B
DE | DE40C | DEAG_BB60 | DETP_BB60 | Friedland | 52.1106 | 14.2461 | 7500 | 4863 | NO | 30.3938 | 0 | 0 | 0 | 176.2837 | 1057.7025 | DE40 | C
DE | DE40A | DEAG_BB64 | DETP_BB64 | Fürstenberg/Bredereiche | 53.1444 | 13.2272 | 8000 | 5814 | NO | 36.3375 | 0 | 0 | 0 | 210.7575 | 1264.545 | DE40 | C
DE | DE40C | DEAG_BB65 | DETP_BB65 | Fürstenwalde | 52.3783 | 14.0088 | 60000 | 47359 | YES | 295.9938 | 947.18 | 710.385 | 1420.77 | 1716.7638 | 10300.5825 | DE40 | C
DE | DE40I | DEAG_BB68 | DETP_BB68 | Gartz | 53.2171 | 14.4025 | 6000 | 4890 | NO | 30.5625 | 0 | 0 | 0 | 177.2625 | 1063.575 | DE40 | B
DE | DE40F | DEAG_BB7 | DETP_BB7 | Bad Wilsnack | 52.9638 | 11.9443 | 6000 | 2631 | NO | 16.4438 | 0 | 0 | 0 | 95.3738 | 572.2425 | DE40 | B
DE | DE40I | DEAG_BB72 | DETP_BB72 | Gerswalde | 53.1622 | 13.7672 | 5000 | 3105 | NO | 19.4062 | 0 | 0 | 0 | 112.5562 | 675.3375 | DE40 | C
DE | DE40H | DEAG_BB8 | DETP_BB8 | Baruth | 52.0419 | 13.5252 | 8000 | 3234 | NO | 20.2125 | 0 | 0 | 0 | 117.2325 | 703.395 | DE40 | C
DE | DE40B | DEAG_BB9 | DETP_BB9 | BASF Schwarzheide | 51.4828 | 13.8979 | 15000 | 14639 | NO | 91.4937 | 0 | 0 | 0 | 530.6637 | 3183.9825 | DE40 | A
DE | DE40B | DEAG_BB90 | DETP_BB90 | Großräschen | 51.578 | 14.0329 | 25000 | 13388 | NO | 83.675 | 0 | 0 | 0 | 485.315 | 2911.89 | DE40 | A
DE | DE40A | DEAG_BB91 | DETP_BB91 | Grüneberg-Hallegraben | 52.8622 | 13.2384 | 12000 | 8116 | NO | 50.725 | 0 | 0 | 0 | 294.205 | 1765.23 | DE40 | C
DE | DE21M | DEAG_BYTS-K0036 | DETP_BYTS-K0036 | Waging/See | 47.9279 | 12.8309 | 32500 | 37021 | NO | 231.3813 | 0 | 0 | 0 | 1342.0113 | 8052.0675 | DE21 | C
DE | DE215 | DEAG_BYTS-K0037 | DETP_BYTS-K0037 | ZV Saalachtal Sitz Piding | 47.7659 | 12.9184 | 18000 | 38149 | NO | 238.4313 | 0 | 0 | 0 | 1382.9012 | 8297.4075 | DE21 | A
DE | DE215 | DEAG_BYTS-K0040 | DETP_BYTS-K0040 | Teisendorf | 47.8541 | 12.833 | 9000 | 11183 | NO | 69.8937 | 0 | 0 | 0 | 405.3837 | 2432.3025 | DE21 | B
DE | DE215 | DEAG_BYTS-K0041 | DETP_BYTS-K0041 | Bayerisch Gmain | 47.729 | 12.9063 | 12000 | 6930 | NO | 43.3125 | 0 | 0 | 0 | 251.2125 | 1507.275 | DE21 | B
DE | DE215 | DEAG_BYTS-K0042 | DETP_BYTS-K0042 | Freilassing | 47.8432 | 12.9895 | 32000 | 28410 | NO | 177.5625 | 0 | 0 | 0 | 1029.8625 | 6179.175 | DE21 | A
DE | DE215 | DEAG_BYTS-K0051 | DETP_BYTS-K0051 | Bad Reichenhall | 47.7641 | 12.9249 | 58000 | 33831 | YES | 211.4438 | 676.62 | 507.465 | 1014.93 | 1226.3737 | 7358.2425 | DE21 | A
DE | DE215 | DEAG_BYTS-K0055 | DETP_BYTS-K0055 | Berchtesgaden | 47.6481 | 13.0355 | 60000 | 43008 | YES | 268.8 | 860.16 | 645.12 | 1290.24 | 1559.04 | 9354.24 | DE21 | C
DE | DE233 | DEAG_BYWEN-K0001 | DETP_BYWEN-K0001 | Weiden i. d. Opf. | 49.6618 | 12.1606 | 100000 | 53475 | YES | 334.2188 | 1069.5 | 802.125 | 1604.25 | 1938.4687 | 11630.8125 | DE23 | A
DE | DE237 | DEAG_BYWEN-K0006 | DETP_BYWEN-K0006 | AZV Weiherhammer u. Mantel | 49.6335 | 12.0708 | 9500 | 7095 | NO | 44.3438 | 0 | 0 | 0 | 257.1938 | 1543.1625 | DE23 | B
DE | DE237 | DEAG_BYWEN-K0008 | DETP_BYWEN-K0008 | Pressath | 49.754 | 11.9459 | 7900 | 4173 | NO | 26.0813 | 0 | 0 | 0 | 151.2713 | 907.6275 | DE23 | B
DE | DE237 | DEAG_BYWEN-K0010 | DETP_BYWEN-K0010 | Eslarn | 49.5861 | 12.5116 | 5800 | 2865 | NO | 17.9062 | 0 | 0 | 0 | 103.8562 | 623.1375 | DE23 | A
DE | DE237 | DEAG_BYWEN-K0013 | DETP_BYWEN-K0013 | Grafenwöhr | 49.7087 | 11.9313 | 25000 | 18890 | NO | 118.0625 | 0 | 0 | 0 | 684.7625 | 4108.575 | DE23 | A
DE | DE237 | DEAG_BYWEN-K0015 | DETP_BYWEN-K0015 | Floß | 49.7293 | 12.269 | 9000 | 5146 | NO | 32.1625 | 0 | 0 | 0 | 186.5425 | 1119.255 | DE23 | B
DE | DE237 | DEAG_BYWEN-K0022 | DETP_BYWEN-K0022 | Windischeschenbach | 49.7912 | 12.168 | 12000 | 9172 | NO | 57.325 | 0 | 0 | 0 | 332.485 | 1994.91 | DE23 | A
DE | DE405 | DEAG_BE02 | DETP_BE02 | Schönerlinde | 52.6512 | 13.4223 | 840000 | 841089 | YES | 5256.8063 | 16821.78 | 12616.335 | 25232.67 | 30489.4763 | 182936.8575 | DE40 | A
DE | DE300 | DEAG_BE03 | DETP_BE03 | Waßmannsdorf | 52.3852 | 13.4646 | 1400000 | 2023000 | YES | 12643.75 | 40460 | 30345 | 60690 | 73333.75 | 440002.5 | DE40 | A
DE | DE80N | DEAG_MV01.01.1 wbu980 | DETP_MV01.01.1 wbu980 | Greifswald | 54.1158 | 13.439 | 96000 | 83834 | YES | 523.9625 | 1676.68 | 1257.51 | 2515.02 | 3038.9825 | 18233.895 | DE80 | C
DE | DE237 | DEAG_BYWEN-K0024 | DETP_BYWEN-K0024 | AZV Pirk-Schirmitz | 49.6345 | 12.1515 | 8500 | 3930 | NO | 24.5625 | 0 | 0 | 0 | 142.4625 | 854.775 | DE23 | B
DE | DE237 | DEAG_BYWEN-K0025 | DETP_BYWEN-K0025 | Pleystein | 49.6469 | 12.4202 | 7500 | 3230 | NO | 20.1875 | 0 | 0 | 0 | 117.0875 | 702.525 | DE23 | B
DE | DE80J | DEAG_MV02.02.1 wbu147 | DETP_MV02.02.1 wbu147 | Neubrandenburg | 53.5681 | 13.2421 | 140000 | 67928 | YES | 424.55 | 1358.56 | 1018.92 | 2037.84 | 2462.39 | 14774.34 | DE80 | A
DE | DE803 | DEAG_MV03.03.1 wbu1437 | DETP_MV03.03.1 wbu1437 | Rostock - Bramow | 54.1042 | 12.0963 | 400000 | 325903 | YES | 2036.8938 | 6518.06 | 4888.545 | 9777.09 | 11813.9837 | 70883.9025 | DE80 | A
DE | DE804 | DEAG_MV04.04.2 wbu1228 | DETP_MV04.04.2 wbu1228 | Schwerin Süd | 53.5235 | 11.358 | 200000 | 158151 | YES | 988.4438 | 3163.02 | 2372.265 | 4744.53 | 5732.9738 | 34397.8425 | DE80 | C
DE | DE80L | DEAG_MV05.05.1 wbu399 | DETP_MV05.05.1 wbu399 | Stralsund | 54.2985 | 13.1007 | 85000 | 91759 | YES | 573.4937 | 1835.18 | 1376.385 | 2752.77 | 3326.2637 | 19957.5825 | DE80 | A
DE | DE237 | DEAG_BYWEN-K0044 | DETP_BYWEN-K0044 | Vohenstrauß | 49.6048 | 12.307 | 17500 | 7617 | NO | 47.6062 | 0 | 0 | 0 | 276.1162 | 1656.6975 | DE23 | C
DE | DE237 | DEAG_BYWEN-K0050 | DETP_BYWEN-K0050 | Eschenbach | 49.7585 | 11.85 | 13000 | 8693 | NO | 54.3313 | 0 | 0 | 0 | 315.1213 | 1890.7275 | DE23 | A
DE | DE237 | DEAG_BYWEN-K0076 | DETP_BYWEN-K0076 | AZV Altenstadt - Neustadt - Störnstein | 49.7118 | 12.1705 | 30000 | 15610 | NO | 97.5625 | 0 | 0 | 0 | 565.8625 | 3395.175 | DE23 | B
DE | DE23A | DEAG_BYWEN-K0092 | DETP_BYWEN-K0092 | Waldsassen | 50.0065 | 12.3145 | 13000 | 10558 | NO | 65.9875 | 0 | 0 | 0 | 382.7275 | 2296.365 | DE23 | A
DE | DE23A | DEAG_BYWEN-K0097 | DETP_BYWEN-K0097 | Friedenfels | 49.8776 | 12.118 | 7000 | 2941 | NO | 18.3813 | 0 | 0 | 0 | 106.6112 | 639.6675 | DE23 | C
DE | DE214 | DEAG_BYTS-K0011 | DETP_BYTS-K0011 | Emmerting-Mehring | 48.2092 | 12.7807 | 7000 | 4112 | NO | 25.7 | 0 | 0 | 0 | 149.06 | 894.36 | DE21 | C
DE | DE214 | DEAG_BYTS-K0014 | DETP_BYTS-K0014 | Burgkirchen/Alz | 48.1783 | 12.7477 | 14000 | 11395 | NO | 71.2188 | 0 | 0 | 0 | 413.0687 | 2478.4125 | DE21 | A
DE | DE21M | DEAG_BYTS-K0016 | DETP_BYTS-K0016 | Reit Im Winkl | 47.6676 | 12.4566 | 14000 | 6117 | NO | 38.2313 | 0 | 0 | 0 | 221.7413 | 1330.4475 | DE21 | C
DE | DE21M | DEAG_BYTS-K0017 | DETP_BYTS-K0017 | Bergen | 47.8176 | 12.5857 | 7500 | 5635 | NO | 35.2188 | 0 | 0 | 0 | 204.2687 | 1225.6125 | DE21 | A
DE | DE21M | DEAG_BYTS-K0021 | DETP_BYTS-K0021 | Traunstein | 47.8865 | 12.6388 | 99000 | 75830 | YES | 473.9375 | 1516.6 | 1137.45 | 2274.9 | 2748.8375 | 16493.025 | DE21 | A
DE | DE21M | DEAG_BYTS-K0023 | DETP_BYTS-K0023 | Inzell | 47.7627 | 12.7373 | 13000 | 9623 | NO | 60.1438 | 0 | 0 | 0 | 348.8338 | 2093.0025 | DE21 | A
DE | DE21M | DEAG_BYTS-K0024 | DETP_BYTS-K0024 | Traunreut OT Stein/Traun | 47.9793 | 12.5484 | 7500 | 9309 | NO | 58.1813 | 0 | 0 | 0 | 337.4513 | 2024.7075 | DE21 | A
DE | DE21M | DEAG_BYTS-K0027 | DETP_BYTS-K0027 | Engelsberg | 48.1102 | 12.5738 | 10000 | 7185 | NO | 44.9062 | 0 | 0 | 0 | 260.4562 | 1562.7375 | DE21 | B
DE | DE21M | DEAG_BYTS-K0029 | DETP_BYTS-K0029 | Tacherting | 48.0872 | 12.5734 | 9000 | 6435 | NO | 40.2188 | 0 | 0 | 0 | 233.2687 | 1399.6125 | DE21 | B
DE | DE21M | DEAG_BYTS-K0030 | DETP_BYTS-K0030 | Ruhpolding | 47.7735 | 12.644 | 20000 | 10212 | NO | 63.825 | 0 | 0 | 0 | 370.185 | 2221.11 | DE21 | A
DE | DE21M | DEAG_BYTS-K0031 | DETP_BYTS-K0031 | Traunreut | 47.9528 | 12.5875 | 35000 | 41151 | NO | 257.1938 | 0 | 0 | 0 | 1491.7238 | 8950.3425 | DE21 | B
DE | DE21M | DEAG_BYTS-K0032 | DETP_BYTS-K0032 | Tittmoning | 48.0667 | 12.764 | 8200 | 6083 | NO | 38.0188 | 0 | 0 | 0 | 220.5088 | 1323.0525 | DE21 | A
DE | DE21M | DEAG_BYTS-K0033 | DETP_BYTS-K0033 | Altenmarkt/Alz | 48.0062 | 12.5375 | 13000 | 11115 | NO | 69.4688 | 0 | 0 | 0 | 402.9187 | 2417.5125 | DE21 | A
DE | DE21M | DEAG_BYTS-K0034 | DETP_BYTS-K0034 | AZV Achental Sitz Grassau | 47.7932 | 12.4857 | 25000 | 18641 | NO | 116.5063 | 0 | 0 | 0 | 675.7363 | 4054.4175 | DE21 | C
DE | DE21M | DEAG_BYTS-K0035 | DETP_BYTS-K0035 | Trostberg | 48.0412 | 12.5693 | 25000 | 13175 | NO | 82.3438 | 0 | 0 | 0 | 477.5938 | 2865.5625 | DE21 | A
DE | DE221 | DEAG_BYLA-K0001 | DETP_BYLA-K0001 | Klärwerk Landshut | 48.5855 | 12.2376 | 260000 | 103733 | YES | 648.3313 | 2074.66 | 1555.995 | 3111.99 | 3760.3212 | 22561.9275 | DE22 | C
DE | DE226 | DEAG_BYLA-K0005 | DETP_BYLA-K0005 | Mainburg | 48.6572 | 11.7906 | 27000 | 16212 | NO | 101.325 | 0 | 0 | 0 | 587.685 | 3526.11 | DE22 | B
DE | DE226 | DEAG_BYLA-K0010 | DETP_BYLA-K0010 | Riedenburg | 48.9589 | 11.6969 | 12000 | 13646 | NO | 85.2875 | 0 | 0 | 0 | 494.6675 | 2968.005 | DE22 | A
DE | DE226 | DEAG_BYLA-K0015 | DETP_BYLA-K0015 | Neustadt/Donau | 48.8171 | 11.766 | 18000 | 28895 | NO | 180.5938 | 0 | 0 | 0 | 1047.4437 | 6284.6625 | DE22 | B
DE | DE226 | DEAG_BYLA-K0016 | DETP_BYLA-K0016 | ZV Im Raume Kelheim Sitz Kelheim | 48.9086 | 11.9309 | 70000 | 45003 | YES | 281.2688 | 900.06 | 675.045 | 1350.09 | 1631.3587 | 9788.1525 | DE22 | A
DE | DE226 | DEAG_BYLA-K0017 | DETP_BYLA-K0017 | Langquaid | 48.8308 | 12.0952 | 8500 | 6347 | NO | 39.6688 | 0 | 0 | 0 | 230.0787 | 1380.4725 | DE22 | C
DE | DE226 | DEAG_BYLA-K0019 | DETP_BYLA-K0019 | Siegenburg | 48.763 | 11.8429 | 5600 | 6978 | NO | 43.6125 | 0 | 0 | 0 | 252.9525 | 1517.715 | DE22 | B
DE | DE226 | DEAG_BYLA-K0025 | DETP_BYLA-K0025 | Bad Abbach | 48.9366 | 12.0288 | 16000 | 14005 | NO | 87.5312 | 0 | 0 | 0 | 507.6812 | 3046.0875 | DE22 | B
DE | DE226 | DEAG_BYLA-K0030 | DETP_BYLA-K0030 | Abensberg | 48.8189 | 11.8304 | 24800 | 16453 | NO | 102.8313 | 0 | 0 | 0 | 596.4212 | 3578.5275 | DE22 | A
DE | DE227 | DEAG_BYLA-K0035 | DETP_BYLA-K0035 | Hohenthann | 48.6604 | 12.0797 | 9999 | 10177 | NO | 63.6062 | 0 | 0 | 0 | 368.9162 | 2213.4975 | DE22 | B
DE | DE227 | DEAG_BYLA-K0041 | DETP_BYLA-K0041 | Velden | 48.3773 | 12.2691 | 7000 | 3940 | NO | 24.625 | 0 | 0 | 0 | 142.825 | 856.95 | DE22 | C
DE | DE227 | DEAG_BYLA-K0051 | DETP_BYLA-K0051 | Geisenhausen | 48.4746 | 12.2693 | 7000 | 5657 | NO | 35.3563 | 0 | 0 | 0 | 205.0662 | 1230.3975 | DE22 | A
DE | DE227 | DEAG_BYLA-K0065 | DETP_BYLA-K0065 | Binabiburg | 48.4428 | 12.4301 | 5000 | 4374 | NO | 27.3375 | 0 | 0 | 0 | 158.5575 | 951.345 | DE22 | B
DE | DE227 | DEAG_BYLA-K0066 | DETP_BYLA-K0066 | ZV AW Ergoldsbach-Neufahrn S.Ergoldsbach | 48.7397 | 12.1883 | 16000 | 14298 | NO | 89.3625 | 0 | 0 | 0 | 518.3025 | 3109.815 | DE22 | A
DE | DE227 | DEAG_BYLA-K0067 | DETP_BYLA-K0067 | Pfeffenhausen | 48.6707 | 11.9732 | 7500 | 5242 | NO | 32.7625 | 0 | 0 | 0 | 190.0225 | 1140.135 | DE22 | A
DE | DE23A | DEAG_BYWEN-K0111 | DETP_BYWEN-K0111 | Kemnath | 49.8511 | 11.8891 | 50000 | 30683 | YES | 191.7687 | 613.66 | 460.245 | 920.49 | 1112.2587 | 6673.5525 | DE23 | C
DE | DE23A | DEAG_BYWEN-K0114 | DETP_BYWEN-K0114 | Neusorg | 49.914 | 11.9715 | 5000 | 2740 | NO | 17.125 | 0 | 0 | 0 | 99.325 | 595.95 | DE23 | C
DE | DE23A | DEAG_BYWEN-K0123 | DETP_BYWEN-K0123 | Wiesau | 49.8847 | 12.2132 | 10000 | 6339 | NO | 39.6187 | 0 | 0 | 0 | 229.7887 | 1378.7325 | DE23 | C
DE | DE23A | DEAG_BYWEN-K0126 | DETP_BYWEN-K0126 | Erbendorf | 49.8341 | 12.0684 | 7800 | 5292 | NO | 33.075 | 0 | 0 | 0 | 191.835 | 1151.01 | DE23 | A
DE | DE23A | DEAG_BYWEN-K0128 | DETP_BYWEN-K0128 | Mitterteich | 49.9545 | 12.2517 | 22000 | 22376 | NO | 139.85 | 0 | 0 | 0 | 811.13 | 4866.78 | DE23 | B
DE | DE23A | DEAG_BYWEN-K0129 | DETP_BYWEN-K0129 | Tirschenreuth | 49.8826 | 12.3099 | 25000 | 15141 | NO | 94.6313 | 0 | 0 | 0 | 548.8613 | 3293.1675 | DE23 | A
DE | DE237 | DEAG_BYWEN-K0132 | DETP_BYWEN-K0132 | Moosbach | 49.5908 | 12.384 | 5225 | 2372 | NO | 14.825 | 0 | 0 | 0 | 85.985 | 515.91 | DE23 | C
DE | DE234 | DEAG_BYWEN-K0136 | DETP_BYWEN-K0136 | Auerbach Opf. | 49.7006 | 11.6243 | 8000 | 8313 | NO | 51.9563 | 0 | 0 | 0 | 301.3462 | 1808.0775 | DE23 | B
DE | DE234 | DEAG_BYWEN-K0137 | DETP_BYWEN-K0137 | Schnaittenbach | 49.5522 | 12.0353 | 7000 | 2708 | NO | 16.925 | 0 | 0 | 0 | 98.165 | 588.99 | DE23 | C
DE | DE234 | DEAG_BYWEN-K0138 | DETP_BYWEN-K0138 | Vilseck | 49.6044 | 11.7813 | 12000 | 8805 | NO | 55.0312 | 0 | 0 | 0 | 319.1812 | 1915.0875 | DE23 | B
DE | DE234 | DEAG_BYWEN-K0155 | DETP_BYWEN-K0155 | Vilseck Südlager US Streitkräfte | 49.6305 | 11.7988 | 15000 | 5244 | NO | 32.775 | 0 | 0 | 0 | 190.095 | 1140.57 | DE23 | B
DE | DE234 | DEAG_BYWEN-K0158 | DETP_BYWEN-K0158 | Hahnbach | 49.5225 | 11.7983 | 8500 | 6700 | NO | 41.875 | 0 | 0 | 0 | 242.875 | 1457.25 | DE23 | B
DE | DE234 | DEAG_BYWEN-K0159 | DETP_BYWEN-K0159 | Zab Amberg-Kümmersbruck, Sitz Amberg | 49.3791 | 11.9135 | 170000 | 167193 | YES | 1044.9562 | 3343.86 | 2507.895 | 5015.79 | 6060.7463 | 36364.4775 | DE23 | C
DE | DE234 | DEAG_BYWEN-K0165 | DETP_BYWEN-K0165 | ZV Unteres Vilstal, Sitz Rieden | 49.2906 | 11.9408 | 7000 | 5550 | NO | 34.6875 | 0 | 0 | 0 | 201.1875 | 1207.125 | DE23 | B
DE | DE234 | DEAG_BYWEN-K0172 | DETP_BYWEN-K0172 | Sulzbach-Rosenberg | 49.4929 | 11.7879 | 45000 | 33962 | YES | 212.2625 | 679.24 | 509.43 | 1018.86 | 1231.1225 | 7386.735 | DE23 | A
DE | DE234 | DEAG_BYWEN-K0179 | DETP_BYWEN-K0179 | Hirschau | 49.5446 | 11.9674 | 11000 | 3317 | NO | 20.7312 | 0 | 0 | 0 | 120.2412 | 721.4475 | DE23 | A
DE | DE239 | DEAG_BYWEN-K0189 | DETP_BYWEN-K0189 | ZV Sulzbachtal | 49.2023 | 12.2598 | 43000 | 23757 | YES | 148.4813 | 475.14 | 356.355 | 712.71 | 861.1913 | 5167.1475 | DE23 | B
DE | DE239 | DEAG_BYWEN-K0190 | DETP_BYWEN-K0190 | Neunburg v.W. | 49.3587 | 12.3658 | 17000 | 10631 | NO | 66.4438 | 0 | 0 | 0 | 385.3738 | 2312.2425 | DE23 | C
DE | DE239 | DEAG_BYWEN-K0204 | DETP_BYWEN-K0204 | Oberviechtach | 49.4406 | 12.3763 | 16000 | 13476 | NO | 84.225 | 0 | 0 | 0 | 488.505 | 2931.03 | DE23 | C
DE | DE239 | DEAG_BYWEN-K0207 | DETP_BYWEN-K0207 | Nabburg | 49.4343 | 12.1695 | 12500 | 9317 | NO | 58.2312 | 0 | 0 | 0 | 337.7412 | 2026.4475 | DE23 | C
DE | DE239 | DEAG_BYWEN-K0223 | DETP_BYWEN-K0223 | Burglengenfeld | 49.2006 | 12.0191 | 16300 | 14446 | NO | 90.2875 | 0 | 0 | 0 | 523.6675 | 3142.005 | DE23 | B
DE | DE239 | DEAG_BYWEN-K0224 | DETP_BYWEN-K0224 | ZV Maxhütte - Haidhof -Teublitz | 49.2186 | 12.0617 | 19800 | 13116 | NO | 81.975 | 0 | 0 | 0 | 475.455 | 2852.73 | DE23 | B
DE | DE239 | DEAG_BYWEN-K0225 | DETP_BYWEN-K0225 | Schwarzenfeld | 49.3696 | 12.1169 | 20000 | 7811 | NO | 48.8188 | 0 | 0 | 0 | 283.1487 | 1698.8925 | DE23 | C
DE | DE239 | DEAG_BYWEN-K0226 | DETP_BYWEN-K0226 | ZV Schwandorf - Wackersdorf | 49.3022 | 12.1092 | 125000 | 63352 | YES | 395.95 | 1267.04 | 950.28 | 1900.56 | 2296.51 | 13779.06 | DE23 | B
DE | DE239 | DEAG_BYWEN-K0244 | DETP_BYWEN-K0244 | Pfreimd | 49.4787 | 12.1775 | 13500 | 2477 | NO | 15.4813 | 0 | 0 | 0 | 89.7912 | 538.7475 | DE23 | B
DE | DE239 | DEAG_BYWEN-K0248 | DETP_BYWEN-K0248 | Wernberg - Köblitz | 49.5269 | 12.1668 | 11500 | 7399 | NO | 46.2438 | 0 | 0 | 0 | 268.2138 | 1609.2825 | DE23 | B
DE | DE216 | DEAG_BYWM-K0002 | DETP_BYWM-K0002 | Bad Tölz | 47.7784 | 11.5422 | 49000 | 44000 | YES | 275 | 880 | 660 | 1320 | 1595 | 9570 | DE21 | C
DE | DE216 | DEAG_BYWM-K0003 | DETP_BYWM-K0003 | Kochel/See | 47.6629 | 11.3599 | 8400 | 7500 | NO | 46.875 | 0 | 0 | 0 | 271.875 | 1631.25 | DE21 | A
DE | DE216 | DEAG_BYWM-K0004 | DETP_BYWM-K0004 | Lenggries | 47.6976 | 11.5642 | 20000 | 14000 | NO | 87.5 | 0 | 0 | 0 | 507.5 | 3045 | DE21 | B
DE | DE216 | DEAG_BYWM-K0007 | DETP_BYWM-K0007 | Benediktbeuern/Bichl | 47.7207 | 11.3963 | 14500 | 6900 | NO | 43.125 | 0 | 0 | 0 | 250.125 | 1500.75 | DE21 | C
DE | DE80M | DEAG_MV58.50.3 wbu706 | DETP_MV58.50.3 wbu706 | Kirchdorf | 53.9957 | 11.4463 | 10000 | 4978 | NO | 31.1125 | 0 | 0 | 0 | 180.4525 | 1082.715 | DE80 | B
DE | DE80M | DEAG_MV58.65.1 wbu664 | DETP_MV58.65.1 wbu664 | Lüdersdorf | 53.828 | 10.779 | 13000 | 11794 | NO | 73.7125 | 0 | 0 | 0 | 427.5325 | 2565.195 | DE80 | C
DE | DE80M | DEAG_MV58.71.1 wbu585 | DETP_MV58.71.1 wbu585 | Mühlen Eichsen | 53.7663 | 11.2473 | 5000 | 2846 | NO | 17.7875 | 0 | 0 | 0 | 103.1675 | 619.005 | DE80 | C
DE | DE80M | DEAG_MV58.74.1 wbu1348 | DETP_MV58.74.1 wbu1348 | Neukloster | 53.844 | 11.6711 | 7900 | 6226 | NO | 38.9125 | 0 | 0 | 0 | 225.6925 | 1354.155 | DE80 | C
DE | DE80N | DEAG_MV59.02.1 wbu2387 | DETP_MV59.02.1 wbu2387 | Anklam | 53.8609 | 13.7233 | 50000 | 21969 | YES | 137.3063 | 439.38 | 329.535 | 659.07 | 796.3763 | 4778.2575 | DE80 | B
DE | DE80N | DEAG_MV59.101.1 wbu2073 | DETP_MV59.101.1 wbu2073 | Wolgast | 54.0607 | 13.7328 | 40000 | 22789 | YES | 142.4313 | 455.78 | 341.835 | 683.67 | 826.1012 | 4956.6075 | DE80 | C
DE | DE80N | DEAG_MV59.107.2 wbu1050 | DETP_MV59.107.2 wbu1050 | Zinnowitz | 54.0546 | 13.9135 | 20000 | 13977 | NO | 87.3563 | 0 | 0 | 0 | 506.6662 | 3039.9975 | DE80 | C
DE | DE216 | DEAG_BYWM-K0015 | DETP_BYWM-K0015 | AV Isar-Loisachgruppe Sitz Wolfratshausen | 47.9263 | 11.4292 | 120000 | 92000 | YES | 575 | 1840 | 1380 | 2760 | 3335 | 20010 | DE21 | B
DE | DE216 | DEAG_BYWM-K0016 | DETP_BYWM-K0016 | Eurasburg | 47.861 | 11.4159 | 9333 | 5700 | NO | 35.625 | 0 | 0 | 0 | 206.625 | 1239.75 | DE21 | B
DE | DE21D | DEAG_BYWM-K0029 | DETP_BYWM-K0029 | Oberammergau | 47.605 | 11.0583 | 15500 | 8100 | NO | 50.625 | 0 | 0 | 0 | 293.625 | 1761.75 | DE21 | A
DE | DE21D | DEAG_BYWM-K0032 | DETP_BYWM-K0032 | Bad Kohlgrub | 47.6646 | 11.081 | 8000 | 3500 | NO | 21.875 | 0 | 0 | 0 | 126.875 | 761.25 | DE21 | C
DE | DE21D | DEAG_BYWM-K0045 | DETP_BYWM-K0045 | Ohlstadt | 47.6349 | 11.2144 | 6000 | 4230 | NO | 26.4375 | 0 | 0 | 0 | 153.3375 | 920.025 | DE21 | B
DE | DE21D | DEAG_BYWM-K0048 | DETP_BYWM-K0048 | Garmisch-Partenkirchen | 47.51 | 11.0985 | 73300 | 49000 | YES | 306.25 | 980 | 735 | 1470 | 1776.25 | 10657.5 | DE21 | A
DE | DE21D | DEAG_BYWM-K0051 | DETP_BYWM-K0051 | Murnau/Staffelsee | 47.6674 | 11.2236 | 50000 | 24000 | YES | 150 | 480 | 360 | 720 | 870 | 5220 | DE21 | B
DE | DE21D | DEAG_BYWM-K0054 | DETP_BYWM-K0054 | Oberes Isartal - Mittenwald | 47.4695 | 11.2792 | 43000 | 22000 | YES | 137.5 | 440 | 330 | 660 | 797.5 | 4785 | DE21 | C
DE | DE21E | DEAG_BYWM-K0058 | DETP_BYWM-K0058 | Landsberg/Lech | 48.0666 | 10.8748 | 64000 | 46000 | YES | 287.5 | 920 | 690 | 1380 | 1667.5 | 10005 | DE21 | A
DE | DE21E | DEAG_BYWM-K0059 | DETP_BYWM-K0059 | ZV Geltendorf-Eresing Sitz Geltendorf | 48.162 | 10.9803 | 9500 | 13500 | NO | 84.375 | 0 | 0 | 0 | 489.375 | 2936.25 | DE21 | C
DE | DE21E | DEAG_BYWM-K0062 | DETP_BYWM-K0062 | Abwasserzweckverband Penzing-Weil Sitz Penzing | 48.1282 | 10.9382 | 12000 | 7100 | NO | 44.375 | 0 | 0 | 0 | 257.375 | 1544.25 | DE21 | C
DE | DE21E | DEAG_BYWM-K0063 | DETP_BYWM-K0063 | Ammerseewerke gKU | 48.0804 | 11.1235 | 90000 | 92000 | YES | 575 | 1840 | 1380 | 2760 | 3335 | 20010 | DE21 | A
DE | DE21N | DEAG_BYWM-K0066 | DETP_BYWM-K0066 | Schongau | 47.816 | 10.9167 | 40000 | 23500 | YES | 146.875 | 470 | 352.5 | 705 | 851.875 | 5111.25 | DE21 | B
DE | DE21N | DEAG_BYWM-K0068 | DETP_BYWM-K0068 | Peißenberg | 47.784 | 11.0795 | 27000 | 13000 | NO | 81.25 | 0 | 0 | 0 | 471.25 | 2827.5 | DE21 | A
DE | DE21N | DEAG_BYWM-K0074 | DETP_BYWM-K0074 | Peiting | 47.8228 | 10.9311 | 25000 | 16000 | NO | 100 | 0 | 0 | 0 | 580 | 3480 | DE21 | B
DE | DE21N | DEAG_BYWM-K0080 | DETP_BYWM-K0080 | Verbandskläranlage Penzberg GmbH | 47.7559 | 11.3996 | 38500 | 20500 | NO | 128.125 | 0 | 0 | 0 | 743.125 | 4458.75 | DE21 | C
DE | DE21N | DEAG_BYWM-K0081 | DETP_BYWM-K0081 | Weilheim/Ob | 47.853 | 11.1434 | 40000 | 34000 | YES | 212.5 | 680 | 510 | 1020 | 1232.5 | 7395 | DE21 | A
DE | DE21E | DEAG_BYWM-K0084 | DETP_BYWM-K0084 | Kaufering | 48.11 | 10.8576 | 18500 | 13500 | NO | 84.375 | 0 | 0 | 0 | 489.375 | 2936.25 | DE21 | C
DE | DE21N | DEAG_BYWM-K0088 | DETP_BYWM-K0088 | ZV Hungerbachtal | 47.779 | 11.111 | 7000 | 5300 | NO | 33.125 | 0 | 0 | 0 | 192.125 | 1152.75 | DE21 | C
DE | DE21L | DEAG_BYWM-K0097 | DETP_BYWM-K0097 | AV Starnberger See Sitz Starnberg | 48.015 | 11.3565 | 100000 | 46000 | YES | 287.5 | 920 | 690 | 1380 | 1667.5 | 10005 | DE21 | B
DE | DED52 | DEAG_SN3362 | DETP_SN33 | Bad Lausick | 51.1455 | 12.626 | 9500 | 7455 | NO | 46.5938 | 0 | 0 | 0 | 270.2437 | 1621.4625 | DED5 | A
DE | DED44 |  | DETP_SN4001 | KA Adorf | 50.3396 | 12.251 | 15000 | 15798 | NO | 98.7375 | 0 | 0 | 0 | 572.6775 | 3436.065 | DED4 | C
DE | DED45 | DEAG_SN4011 | DETP_SN4022 | ZKA Crimmitschau | 50.8371 | 12.3953 | 28000 | 36200 | NO | 226.25 | 0 | 0 | 0 | 1312.25 | 7873.5 | DED4 | A
DE | DED45 | DEAG_SN4121 | DETP_SN4025 | KA Cunersdorf | 50.6523 | 12.5238 | 13500 | 14800 | NO | 92.5 | 0 | 0 | 0 | 536.5 | 3219 | DED4 | C
DE | DED45 | DEAG_SN4120 | DETP_SN4037 | KA Niederopritz | 50.6496 | 12.6404 | 9000 | 4367 | NO | 27.2938 | 0 | 0 | 0 | 158.3038 | 949.8225 | DED4 | C
DE | DED52 |  | DETP_SN404 | Kleindalzig | 51.2028 | 12.3047 | 24000 | 23607 | NO | 147.5438 | 0 | 0 | 0 | 855.7538 | 5134.5225 | DED5 | C
DE | DED44 | DEAG_SN4111 | DETP_SN4047 | ZKA Klingenthal | 50.3468 | 12.4822 | 11500 | 7455 | NO | 46.5938 | 0 | 0 | 0 | 270.2437 | 1621.4625 | CZ04 | C
DE | DE300 | DEAG_BE01 | DETP_BE01 | Ruhleben | 52.5316 | 13.2317 | 1600000 | 1901188 | NO | 11882.425 | 0 | 0 | 0 | 68918.065 | 413508.39 | DE30 | A
DE | DE40E | DEAG_BB10 | DETP_BB10 | Beelitz | 52.2296 | 12.981 | 30000 | 16510 | NO | 103.1875 | 0 | 0 | 0 | 598.4875 | 3590.925 | DE40 | A
DE | DE407 | DEAG_BB105 | DETP_BB105 | Herzberg | 51.7112 | 13.2208 | 25000 | 9647 | NO | 60.2937 | 0 | 0 | 0 | 349.7037 | 2098.2225 | DE40 | C
DE | DE40E | DEAG_BB118 | DETP_BB118 | Jeserig | 52.401 | 12.6747 | 16000 | 11146 | NO | 69.6625 | 0 | 0 | 0 | 404.0425 | 2424.255 | DE40 | C
DE | DE40C | DEAG_BB12 | DETP_BB12 | Beeskow | 52.1955 | 14.2576 | 15500 | 11408 | NO | 71.3 | 0 | 0 | 0 | 413.54 | 2481.24 | DE40 | A
DE | DE405 | DEAG_BB120 | DETP_BB120 | Joachimsthal | 52.962 | 13.7739 | 15000 | 5016 | NO | 31.35 | 0 | 0 | 0 | 181.83 | 1090.98 | DE40 | C
DE | DE40H | DEAG_BB121 | DETP_BB121 | Jüterbog | 52.0004 | 13.1014 | 29000 | 18759 | NO | 117.2437 | 0 | 0 | 0 | 680.0137 | 4080.0825 | DE40 | B
DE | DE40F | DEAG_BB123 | DETP_BB123 | Karstädt | 53.1564 | 11.7264 | 10000 | 3190 | NO | 19.9375 | 0 | 0 | 0 | 115.6375 | 693.825 | DE40 | C
DE | DE406 | DEAG_BB124 | DETP_BB124 | Kasel-Golzig | 51.9265 | 13.7138 | 48000 | 14964 | YES | 93.525 | 299.28 | 224.46 | 448.92 | 542.445 | 3254.67 | DE40 | C
DE | DE40E | DEAG_BB126 | DETP_BB126 | Werder OT Kemnitz | 52.415 | 12.9031 | 38000 | 27557 | YES | 172.2313 | 551.14 | 413.355 | 826.71 | 998.9413 | 5993.6475 | DE40 | A
DE | DE40E | DEAG_BB13 | DETP_BB13 | Belzig | 52.1463 | 12.604 | 10000 | 9216 | NO | 57.6 | 0 | 0 | 0 | 334.08 | 2004.48 | DE40 | A
DE | DE40A | DEAG_BB137 | DETP_BB137 | Kremmen | 52.7608 | 13.06 | 14400 | 11583 | NO | 72.3937 | 0 | 0 | 0 | 419.8837 | 2519.3025 | DE40 | C
DE | DE40B | DEAG_BB146 | DETP_BB146 | Lauchhammer | 51.4648 | 13.7544 | 27000 | 16285 | NO | 101.7812 | 0 | 0 | 0 | 590.3312 | 3541.9875 | DE40 | B
DE | DE40E | DEAG_BB147 | DETP_BB147 | Lehnin | 52.3216 | 12.7239 | 30000 | 4478 | NO | 27.9875 | 0 | 0 | 0 | 162.3275 | 973.965 | DE40 | B
DE | DE40F | DEAG_BB149 | DETP_BB149 | Lenzen | 53.0934 | 11.4615 | 5632 | 1830 | NO | 11.4375 | 0 | 0 | 0 | 66.3375 | 398.025 | DE40 | B
DE | DE40A | DEAG_BB154 | DETP_BB154 | Liebenwalde | 52.8457 | 13.4008 | 14100 | 18605 | NO | 116.2812 | 0 | 0 | 0 | 674.4312 | 4046.5875 | DE40 | C
DE | DE406 | DEAG_BB159 | DETP_BB159 | Lübben | 51.9431 | 13.9267 | 50000 | 13894 | YES | 86.8375 | 277.88 | 208.41 | 416.82 | 503.6575 | 3021.945 | DE40 | A
DE | DE40B | DEAG_BB160 | DETP_BB160 | Lübbenau/Spreewald | 51.8687 | 13.9321 | 26000 | 13774 | NO | 86.0875 | 0 | 0 | 0 | 499.3075 | 2995.845 | DE40 | B
DE | DE40H | DEAG_BB162 | DETP_BB162 | Luckenwalde | 52.1103 | 13.1559 | 40000 | 26821 | YES | 167.6312 | 536.42 | 402.315 | 804.63 | 972.2613 | 5833.5675 | DE40 | B
DE | DE40H | DEAG_BB163 | DETP_BB163 | Ludwigsfelde | 52.2956 | 13.2784 | 48000 | 27020 | YES | 168.875 | 540.4 | 405.3 | 810.6 | 979.475 | 5876.85 | DE40 | A
DE | DE405 | DEAG_BB165 | DETP_BB165 | Lunow | 52.906 | 14.1319 | 7000 | 4231 | NO | 26.4437 | 0 | 0 | 0 | 153.3737 | 920.2425 | DE40 | C
DE | DE40I | DEAG_BB166 | DETP_BB166 | Lychen | 53.1962 | 13.3225 | 8000 | 3139 | NO | 19.6188 | 0 | 0 | 0 | 113.7888 | 682.7325 | DE40 | A
DE | DE409 | DEAG_BB169 | DETP_BB169 | Manschnow | 52.5596 | 14.5756 | 15000 | 6132 | NO | 38.325 | 0 | 0 | 0 | 222.285 | 1333.71 | DE40 | C
DE | DE409 | DEAG_BB176 | DETP_BB176 | Münchehofe | 52.4886 | 13.6588 | 279300 | 157266 | YES | 982.9125 | 3145.32 | 2358.99 | 4717.98 | 5700.8925 | 34205.355 | DE40 | A
DE | DE408 | DEAG_BB177 | DETP_BB177 | Nauen | 52.6367 | 12.8757 | 21500 | 15754 | NO | 98.4625 | 0 | 0 | 0 | 571.0825 | 3426.495 | DE40 | A
DE | DE408 | DEAG_BB179 | DETP_BB179 | Nennhausen | 52.6017 | 12.5387 | 5000 | 3497 | NO | 21.8562 | 0 | 0 | 0 | 126.7662 | 760.5975 | DE40 | C
DE | DE40D | DEAG_BB182 | DETP_BB182 | Neuruppin | 52.9507 | 12.8153 | 44000 | 31232 | YES | 195.2 | 624.64 | 468.48 | 936.96 | 1132.16 | 6792.96 | DE40 | B
DE | DE40D | DEAG_BB186 | DETP_BB186 | Neustadt (Dosse) | 52.87 | 12.4708 | 30000 | 21373 | NO | 133.5813 | 0 | 0 | 0 | 774.7713 | 4648.6275 | DE40 | A
DE | DE40G | DEAG_BB192 | DETP_BB192 | Peitz | 51.8499 | 14.4138 | 12000 | 9455 | NO | 59.0938 | 0 | 0 | 0 | 342.7437 | 2056.4625 | DE40 | A
DE | DE40F | DEAG_BB193 | DETP_BB193 | Perleberg | 53.0575 | 11.8503 | 80000 | 12546 | YES | 78.4125 | 250.92 | 188.19 | 376.38 | 454.7925 | 2728.755 | DE40 | C
DE | DED44 | DEAG_SN4114 | DETP_SN4050 | KA Kürbitz | 50.4667 | 12.0737 | 7000 | 5088 | NO | 31.8 | 0 | 0 | 0 | 184.44 | 1106.64 | DED4 | B
DE | DED44 | DEAG_SN4112 | DETP_SN4053 | KA Lengenfeld | 50.578 | 12.3522 | 6200 | 7594 | NO | 47.4625 | 0 | 0 | 0 | 275.2825 | 1651.695 | DED4 | A
DE | DED44 | DEAG_SN4009 | DETP_SN4065 | KA Oelsnitz | 50.4179 | 12.15 | 15000 | 13458 | NO | 84.1125 | 0 | 0 | 0 | 487.8525 | 2927.115 | DED4 | A
DE | DED44 | DEAG_SN4001 | DETP_SN4070 | ZKA Plauen | 50.5251 | 12.1691 | 140000 | 112658 | YES | 704.1125 | 2253.16 | 1689.87 | 3379.74 | 4083.8525 | 24503.115 | DED4 | C
DE | DED44 | DEAG_SN4003 | DETP_SN4079 | ZKA Reichenbach | 50.6284 | 12.2387 | 39000 | 24397 | YES | 152.4813 | 487.94 | 365.955 | 731.91 | 884.3913 | 5306.3475 | DED4 | C
DE | DED44 |  | DETP_SN4081 | ZKA Rodewisch | 50.5506 | 12.3843 | 60000 | 65000 | YES | 406.25 | 1300 | 975 | 1950 | 2356.25 | 14137.5 | DED4 | B
DE | DED44 | DEAG_SN4117 | DETP_SN4083 | KA Rothenkirchen | 50.5487 | 12.5147 | 8000 | 5163 | NO | 32.2688 | 0 | 0 | 0 | 187.1587 | 1122.9525 | DED4 | B
DE | DED42 |  | DETP_SN4084 | ZKA Schlematal | 50.6178 | 12.6841 | 73500 | 58781 | YES | 367.3812 | 1175.62 | 881.715 | 1763.43 | 2130.8112 | 12784.8675 | DED4 | B
DE | DED44 | DEAG_SN4116 | DETP_SN4089 | KA Schöneck | 50.3806 | 12.3261 | 5400 | 4062 | NO | 25.3875 | 0 | 0 | 0 | 147.2475 | 883.485 | DED4 | C
DE | DED42 |  | DETP_SN4092 | ZKA Schwarzenberg | 50.5551 | 12.7673 | 37700 | 30049 | NO | 187.8063 | 0 | 0 | 0 | 1089.2762 | 6535.6575 | DED4 | A
DE | DED44 | DEAG_SN4008 | DETP_SN4098 | ZKA Treuen | 50.5254 | 12.284 | 15000 | 12241 | NO | 76.5063 | 0 | 0 | 0 | 443.7363 | 2662.4175 | DED4 | C
DE | DED45 |  | DETP_SN4107 | ZKA Werdau | 50.7478 | 12.3771 | 48000 | 52250 | YES | 326.5625 | 1045 | 783.75 | 1567.5 | 1894.0625 | 11364.375 | DED4 | A
DE | DED42 |  | DETP_SN4109 | ZKA Wolfsgrün | 50.5221 | 12.6103 | 16600 | 13426 | NO | 83.9125 | 0 | 0 | 0 | 486.6925 | 2920.155 | DED4 | C
DE | DED45 |  | DETP_SN4112 | ZKA Zwickau | 50.7693 | 12.4815 | 143000 | 135654 | YES | 847.8375 | 2713.08 | 2034.81 | 4069.62 | 4917.4575 | 29504.745 | DED4 | B
DE | DED44 | DEAG_SN4110 | DETP_SN4125 | ZKA Elsterberg (komm) | 50.6051 | 12.1609 | 6000 | 3125 | NO | 19.5312 | 0 | 0 | 0 | 113.2812 | 679.6875 | DED4 | A
DE | DED2F | DEAG_SN5056 | DETP_SN415 | Königstein | 50.9206 | 14.0668 | 6000 | 5905 | NO | 36.9062 | 0 | 0 | 0 | 214.0562 | 1284.3375 | DED2 | A
DE | DE404 | DEAG_BB200 | DETP_BB200 | Potsdam-Nord | 52.4372 | 13.0262 | 90000 | 73254 | YES | 457.8375 | 1465.08 | 1098.81 | 2197.62 | 2655.4575 | 15932.745 | DE40 | A
DE | DE40I | DEAG_BB207 | DETP_BB207 | Prenzlau | 53.3237 | 13.8531 | 80000 | 24648 | YES | 154.05 | 492.96 | 369.72 | 739.44 | 893.49 | 5360.94 | DE40 | A
DE | DE40F | DEAG_BB209 | DETP_BB209 | Pritzwalk/Schönhagen | 53.1663 | 12.1436 | 30000 | 12981 | NO | 81.1313 | 0 | 0 | 0 | 470.5613 | 2823.3675 | DE40 | B
DE | DE408 | DEAG_BB211 | DETP_BB211 | Rathenow | 52.6281 | 12.3303 | 40000 | 36654 | YES | 229.0875 | 733.08 | 549.81 | 1099.62 | 1328.7075 | 7972.245 | DE40 | C
DE | DE408 | DEAG_BB215 | DETP_BB215 | Roskow | 52.4784 | 12.7449 | 36000 | 31946 | NO | 199.6625 | 0 | 0 | 0 | 1158.0425 | 6948.255 | DE40 | C
DE | DE404 | DEAG_BB219 | DETP_BB219 | Satzkorn | 52.4641 | 12.9882 | 10000 | 8668 | NO | 54.175 | 0 | 0 | 0 | 314.215 | 1885.29 | DE40 | C
DE | DE401 | DEAG_BB22 | DETP_BB22 | Brandenburg - Briest | 52.4179 | 12.4365 | 99000 | 81618 | YES | 510.1125 | 1632.36 | 1224.27 | 2448.54 | 2958.6525 | 17751.915 | DE40 | C
DE | DE40A | DEAG_BB227 | DETP_BB227 | Schönermark OHV | 53.0209 | 13.1146 | 42000 | 21073 | YES | 131.7063 | 421.46 | 316.095 | 632.19 | 763.8963 | 4583.3775 | DE40 | C
DE | DE407 | DEAG_BB229 | DETP_BB229 | Schönewalde | 51.8078 | 13.2145 | 8000 | 2960 | NO | 18.5 | 0 | 0 | 0 | 107.3 | 643.8 | DE40 | B
DE | DE40I | DEAG_BB231 | DETP_BB231 | Schwedt | 53.0549 | 14.2543 | 65000 | 33029 | YES | 206.4313 | 660.58 | 495.435 | 990.87 | 1197.3012 | 7183.8075 | DE40 | A
DE | DE409 | DEAG_BB232 | DETP_BB232 | Seelow | 52.543 | 14.3959 | 17500 | 9947 | NO | 62.1687 | 0 | 0 | 0 | 360.5787 | 2163.4725 | DE40 | A
DE | DE40G | DEAG_BB238 | DETP_BB238 | Spremberg-Nord | 51.5783 | 14.3721 | 50000 | 17639 | YES | 110.2437 | 352.78 | 264.585 | 529.17 | 639.4137 | 3836.4825 | DE40 | A
DE | DE40E | DEAG_BB239 | DETP_BB239 | Stahnsdorf | 52.377 | 13.2482 | 430000 | 188253 | YES | 1176.5812 | 3765.06 | 2823.795 | 5647.59 | 6824.1712 | 40945.0275 | DE40 | A
DE | DE40B | DEAG_BB24 | DETP_BB24 | Brieske/Senftenberg | 51.4939 | 13.9637 | 60000 | 25079 | YES | 156.7438 | 501.58 | 376.185 | 752.37 | 909.1137 | 5454.6825 | DE40 | A
DE | DE40C | DEAG_BB243 | DETP_BB243 | Storkow | 52.2789 | 13.9486 | 32900 | 21266 | YES | 132.9125 | 425.32 | 318.99 | 637.98 | 770.8925 | 4625.355 | DE40 | C
DE | DE406 | DEAG_BB244 | DETP_BB244 | Straupitz | 51.9106 | 14.1031 | 7150 | 3400 | NO | 21.25 | 0 | 0 | 0 | 123.25 | 739.5 | DE40 | C
DE | DE40E | DEAG_BB25 | DETP_BB25 | Brück Hackenhausen | 52.2157 | 12.7408 | 16000 | 11155 | NO | 69.7188 | 0 | 0 | 0 | 404.3687 | 2426.2125 | DE40 | C
DE | DE40I | DEAG_BB250 | DETP_BB250 | Templin | 53.087 | 13.4734 | 22000 | 15340 | NO | 95.875 | 0 | 0 | 0 | 556.075 | 3336.45 | DE40 | C
DE | DE40C | DEAG_BB254 | DETP_BB254 | Trebatsch | 52.1015 | 14.182 | 8000 | 2853 | NO | 17.8313 | 0 | 0 | 0 | 103.4212 | 620.5275 | DE40 | C
DE | DE40H | DEAG_BB255 | DETP_BB255 | Trebbin | 52.2248 | 13.2403 | 10000 | 5992 | NO | 37.45 | 0 | 0 | 0 | 217.21 | 1303.26 | DE40 | B
DE | DE40E | DEAG_BB256 | DETP_BB256 | Treuenbrietzen | 52.1082 | 12.8745 | 10000 | 8893 | NO | 55.5813 | 0 | 0 | 0 | 322.3712 | 1934.2275 | DE40 | B
DE | DE407 | DEAG_BB257 | DETP_BB257 | Uebigau | 51.6084 | 13.3047 | 17000 | 7980 | NO | 49.875 | 0 | 0 | 0 | 289.275 | 1735.65 | DE40 | C
DE | DE40B | DEAG_BB259 | DETP_BB259 | Vetschau | 51.7974 | 14.073 | 18000 | 6131 | NO | 38.3188 | 0 | 0 | 0 | 222.2488 | 1333.4925 | DE40 | B
DE | DE408 | DEAG_BB261 | DETP_BB261 | Wagenitz | 52.6657 | 12.6383 | 6000 | 5035 | NO | 31.4688 | 0 | 0 | 0 | 182.5187 | 1095.1125 | DE40 | C
DE | DE408 | DEAG_BB266 | DETP_BB266 | Wansdorf | 52.6178 | 13.092 | 270000 | 179672 | YES | 1122.95 | 3593.44 | 2695.08 | 5390.16 | 6513.11 | 39078.66 | DE40 | C
DE | DE40G | DEAG_BB27 | DETP_BB27 | Burg | 51.8239 | 14.1608 | 12000 | 10745 | NO | 67.1562 | 0 | 0 | 0 | 389.5062 | 2337.0375 | DE40 | C
DE | DE40D | DEAG_BB272 | DETP_BB272 | Werder | 52.9123 | 12.7009 | 5000 | 2772 | NO | 17.325 | 0 | 0 | 0 | 100.485 | 602.91 | DE40 | A
DE | DE405 | DEAG_BB273 | DETP_BB273 | Werneuchen | 52.6188 | 13.7326 | 15000 | 10824 | NO | 67.65 | 0 | 0 | 0 | 392.37 | 2354.22 | DE40 | C
DE | DE40E | DEAG_BB276 | DETP_BB276 | Wiesenburg/Mark | 52.1047 | 12.4494 | 6000 | 3935 | NO | 24.5938 | 0 | 0 | 0 | 142.6437 | 855.8625 | DE40 | C
DE | DE407 | DEAG_BB279 | DETP_BB279 | Winkel | 51.5453 | 13.4004 | 5000 | 3212 | NO | 20.075 | 0 | 0 | 0 | 116.435 | 698.61 | DE40 | C
DE | DE40F | DEAG_BB280 | DETP_BB280 | Wittenberge | 53.0248 | 11.6993 | 45000 | 19218 | YES | 120.1125 | 384.36 | 288.27 | 576.54 | 696.6525 | 4179.915 | DE40 | C
DE | DE40D | DEAG_BB282 | DETP_BB282 | Wittstock/Dosse | 53.1413 | 12.4773 | 25000 | 14438 | NO | 90.2375 | 0 | 0 | 0 | 523.3775 | 3140.265 | DE40 | A
DE | DE409 | DEAG_BB286 | DETP_BB286 | Wriezen | 52.724 | 14.1472 | 36000 | 24218 | NO | 151.3625 | 0 | 0 | 0 | 877.9025 | 5267.415 | DE40 | A
DE | DE40B | DEAG_BB29 | DETP_BB29 | Calau | 51.7475 | 13.9739 | 8000 | 5153 | NO | 32.2063 | 0 | 0 | 0 | 186.7963 | 1120.7775 | DE40 | A
DE | DE40A | DEAG_BB292 | DETP_BB292 | Zehdenick | 52.967 | 13.3655 | 15000 | 12018 | NO | 75.1125 | 0 | 0 | 0 | 435.6525 | 2613.915 | DE40 | C
DE | DE40E | DEAG_BB293 | DETP_BB293 | Ziesar | 52.2815 | 12.3061 | 6750 | 4338 | NO | 27.1125 | 0 | 0 | 0 | 157.2525 | 943.515 | DE40 | C
DE | DE409 | DEAG_BB3 | DETP_BB3 | Altfriedland | 52.6572 | 14.2007 | 22500 | 18506 | NO | 115.6625 | 0 | 0 | 0 | 670.8425 | 4025.055 | DE40 | C
DE | DE402 | DEAG_BB30 | DETP_BB30 | Cottbus | 51.7734 | 14.3512 | 200000 | 106060 | YES | 662.875 | 2121.2 | 1590.9 | 3181.8 | 3844.675 | 23068.05 | DE40 | A
DE | DE407 | DEAG_BB319 | DETP_BB319 | Großthiemig | 51.3886 | 13.6922 | 6000 | 5573 | NO | 34.8313 | 0 | 0 | 0 | 202.0213 | 1212.1275 | DE40 | C
DE | DE80K | DEAG_MV51.04.1 | DETP_MV51.04.1 | Bad Doberan | 54.1156 | 11.925 | 60000 | 60443 | YES | 377.7688 | 1208.86 | 906.645 | 1813.29 | 2191.0588 | 13146.3525 | DE80 | B
DE | DE80K | DEAG_MV51.41.1 wbu459 | DETP_MV51.41.1 wbu459 | Kröpelin (neu) | 54.0636 | 11.7786 | 10000 | 8539 | NO | 53.3688 | 0 | 0 | 0 | 309.5387 | 1857.2325 | DE80 | A
DE | DE80K | DEAG_MV51.47.1 wbu891 | DETP_MV51.47.1 wbu891 | Neubukow | 54.0296 | 11.6781 | 6000 | 5797 | NO | 36.2313 | 0 | 0 | 0 | 210.1413 | 1260.8475 | DE80 | A
DE | DE80K | DEAG_MV51.71.1 wbu190 | DETP_MV51.71.1 wbu190 | Schwaan | 53.9495 | 12.1099 | 13000 | 13244 | NO | 82.775 | 0 | 0 | 0 | 480.095 | 2880.57 | DE80 | B
DE | DE80J | DEAG_MV52.03.1 wbu144 | DETP_MV52.03.1 wbu144 | Altentreptow | 53.6814 | 13.2537 | 9200 | 2456 | NO | 15.35 | 0 | 0 | 0 | 89.03 | 534.18 | DE80 | B
DE | DE80J | DEAG_MV52.17.1 wbu2230 | DETP_MV52.17.1 wbu2230 | Dargun | 53.8965 | 12.8684 | 90000 | 57739 | YES | 360.8688 | 1154.78 | 866.085 | 1732.17 | 2093.0388 | 12558.2325 | DE80 | B
DE | DE80J | DEAG_MV52.18.1 wbu142 | DETP_MV52.18.1 wbu142 | Demmin | 53.918 | 13.0605 | 30000 | 15207 | NO | 95.0438 | 0 | 0 | 0 | 551.2537 | 3307.5225 | DE80 | B
DE | DE80N | DEAG_MV52.39.1 wbu2538 | DETP_MV52.39.1 wbu2538 | Jarmen | 53.9087 | 13.3756 | 8000 | 3859 | NO | 24.1188 | 0 | 0 | 0 | 139.8888 | 839.3325 | DE80 | C
DE | DE80N | DEAG_MV52.49.3 wbu2542 | DETP_MV52.49.3 wbu2542 | Loitz | 53.9737 | 13.1638 | 8000 | 4579 | NO | 28.6188 | 0 | 0 | 0 | 165.9887 | 995.9325 | DE80 | C
DE | DE80J | DEAG_MV52.74.3 wbu2539 | DETP_MV52.74.3 wbu2539 | Stavenhagen | 53.7036 | 12.9224 | 200000 | 86167 | YES | 538.5438 | 1723.34 | 1292.505 | 2585.01 | 3123.5538 | 18741.3225 | DE80 | B
DE | DEE0A | DEAG_ST152661000004 | DETP_ST152661000004 | Thürungen | 51.4562 | 11.0395 | 14000 | 9466 | NO | 59.1625 | 0 | 0 | 0 | 343.1425 | 2058.855 | DEE0 | C
DE | DEE08 | DEAG_ST152681000001 | DETP_ST152681000001 | Weißenfels | 51.2152 | 11.9849 | 125000 | 55618 | YES | 347.6125 | 1112.36 | 834.27 | 1668.54 | 2016.1525 | 12096.915 | DEE0 | A
DE | DEE08 | DEAG_ST152681000003 | DETP_ST152681000003 | Zembschen | 51.1475 | 12.094 | 11000 | 8680 | NO | 54.25 | 0 | 0 | 0 | 314.65 | 1887.9 | DEE0 | B
DE | DEE08 | DEAG_ST152681000004 | DETP_ST152681000004 | Uichteritz | 51.193 | 11.9167 | 7500 | 6670 | NO | 41.6875 | 0 | 0 | 0 | 241.7875 | 1450.725 | DEE0 | B
DE | DEE08 | DEAG_ST152681000006 | DETP_ST152681000006 | Wengelsdorf | 51.2839 | 12.0484 | 17000 | 18991 | NO | 118.6938 | 0 | 0 | 0 | 688.4238 | 4130.5425 | DEE0 | B
DE | DEE0C | DEAG_ST153521000001 | DETP_ST153521000001 | Aschersleben | 51.7498 | 11.4888 | 48000 | 39188 | YES | 244.925 | 783.76 | 587.82 | 1175.64 | 1420.565 | 8523.39 | DEE0 | A
DE | DEE0C | DEAG_ST153521000002 | DETP_ST153521000002 | Hecklingen | 51.8575 | 11.5572 | 40000 | 25800 | YES | 161.25 | 516 | 387 | 774 | 935.25 | 5611.5 | DEE0 | B
DE | DEE0C | DEAG_ST153521000003 | DETP_ST153521000003 | Hoym | 51.7987 | 11.3066 | 15000 | 10349 | NO | 64.6813 | 0 | 0 | 0 | 375.1513 | 2250.9075 | DEE0 | C
DE | DE40H | DEAG_BB32 | DETP_BB32 | Dahme | 51.8785 | 13.4396 | 7500 | 6656 | NO | 41.6 | 0 | 0 | 0 | 241.28 | 1447.68 | DE40 | A
DE | DE407 | DEAG_BB34 | DETP_BB34 | Lindena | 51.589 | 13.5247 | 25000 | 12287 | NO | 76.7938 | 0 | 0 | 0 | 445.4037 | 2672.4225 | DE40 | C
DE | DE40G | DEAG_BB35 | DETP_BB35 | Döbern | 51.6229 | 14.5991 | 6000 | 5830 | NO | 36.4375 | 0 | 0 | 0 | 211.3375 | 1268.025 | DE40 | B
DE | DE40G | DEAG_BB38 | DETP_BB38 | Drebkau | 51.6652 | 14.2076 | 6000 | 4293 | NO | 26.8313 | 0 | 0 | 0 | 155.6213 | 933.7275 | DE40 | C
DE | DE406 | DEAG_BB4 | DETP_BB4 | Alt-Schadow | 52.1071 | 13.9562 | 12000 | 4054 | NO | 25.3375 | 0 | 0 | 0 | 146.9575 | 881.745 | DE40 | C
DE | DE406 | DEAG_BB40 | DETP_BB40 | Dürrenhofe / Krugau | 52.034 | 13.9716 | 6000 | 3214 | NO | 20.0875 | 0 | 0 | 0 | 116.5075 | 699.045 | DE40 | C
DE | DE405 | DEAG_BB41 | DETP_BB41 | Eberswalde | 52.839 | 13.8388 | 80000 | 53640 | YES | 335.25 | 1072.8 | 804.6 | 1609.2 | 1944.45 | 11666.7 | DE40 | A
DE | DE408 | DEAG_BB412 | DETP_BB412 | MFKE Premnitz | 52.5309 | 12.3608 | 100000 | 7028 | YES | 43.925 | 140.56 | 105.42 | 210.84 | 254.765 | 1528.59 | DE40 | A
DE | DE80K | DEAG_MV53.13.1 wbu437 | DETP_MV53.13.1 wbu437 | Bützow/Wolken | 53.8367 | 12.0146 | 25000 | 26138 | NO | 163.3625 | 0 | 0 | 0 | 947.5025 | 5685.015 | DE80 | B
DE | DE80K | DEAG_MV53.14.1 wbu270 | DETP_MV53.14.1 wbu270 | Krakow - Charlottenthal | 53.6874 | 12.2831 | 7500 | 6287 | NO | 39.2938 | 0 | 0 | 0 | 227.9038 | 1367.4225 | DE80 | C
DE | DE80K | DEAG_MV53.31.1 wbu1060 | DETP_MV53.31.1 wbu1060 | Güstrow/Parum | 53.8177 | 12.1217 | 60000 | 40858 | YES | 255.3625 | 817.16 | 612.87 | 1225.74 | 1481.1025 | 8886.615 | DE80 | C
DE | DE80K | DEAG_MV53.47.1 wbu331 | DETP_MV53.47.1 wbu331 | Laage/Pinnow | 53.9461 | 12.3547 | 20000 | 12387 | NO | 77.4188 | 0 | 0 | 0 | 449.0288 | 2694.1725 | DE80 | C
DE | DE80K | DEAG_MV53.87.1 wbu688 | DETP_MV53.87.1 wbu688 | Teterow | 53.7714 | 12.5993 | 50000 | 36860 | YES | 230.375 | 737.2 | 552.9 | 1105.8 | 1336.175 | 8017.05 | DE80 | B
DE | DE80O | DEAG_MV54.121.1 wbu349 | DETP_MV54.121.1 wbu349 | Zarrentin | 53.5192 | 11.0087 | 56000 | 35860 | YES | 224.125 | 717.2 | 537.9 | 1075.8 | 1299.925 | 7799.55 | DE80 | C
DE | DE80O | DEAG_MV54.13.4 wbu69 | DETP_MV54.13.4 wbu69 | Boizenburg/Elbe | 53.3843 | 10.7625 | 27000 | 18973 | NO | 118.5813 | 0 | 0 | 0 | 687.7713 | 4126.6275 | DE80 | A
DE | DE80O | DEAG_MV54.37.2 wbu405 | DETP_MV54.37.2 wbu405 | Fahlenkamp | 53.2581 | 11.5044 | 40000 | 32018 | YES | 200.1125 | 640.36 | 480.27 | 960.54 | 1160.6525 | 6963.915 | DE80 | C
DE | DE80O | DEAG_MV54.43.1 wbu335 | DETP_MV54.43.1 wbu335 | Hagenow | 53.4258 | 11.1773 | 47600 | 110741 | YES | 692.1313 | 2214.82 | 1661.115 | 3322.23 | 4014.3612 | 24086.1675 | DE80 | A
DE | DE80O | DEAG_MV54.67.2 wbu304 | DETP_MV54.67.2 wbu304 | Lübtheen | 53.3047 | 11.0691 | 6500 | 3137 | NO | 19.6062 | 0 | 0 | 0 | 113.7162 | 682.2975 | DE80 | B
DE | DE80O | DEAG_MV54.79.1 wbu1173 | DETP_MV54.79.1 wbu1173 | Neu Kaliß | 53.182 | 11.3118 | 17400 | 5707 | NO | 35.6688 | 0 | 0 | 0 | 206.8788 | 1241.2725 | DE80 | C
DE | DE80O | DEAG_MV54.81.2 wbu1174 | DETP_MV54.81.2 wbu1174 | Neustadt Glewe | 53.3735 | 11.5784 | 10000 | 8438 | NO | 52.7375 | 0 | 0 | 0 | 305.8775 | 1835.265 | DE80 | A
DE | DE80J | DEAG_MV55.20.2 | DETP_MV55.20.2 | Friedland | 53.6953 | 13.5906 | 11600 | 5186 | NO | 32.4125 | 0 | 0 | 0 | 187.9925 | 1127.955 | DE80 | C
DE | DE80J | DEAG_MV55.44.1 wbu198 | DETP_MV55.44.1 wbu198 | Mirow | 53.257 | 12.8115 | 11750 | 8122 | NO | 50.7625 | 0 | 0 | 0 | 294.4225 | 1766.535 | DE80 | C
DE | DE80J | DEAG_MV55.50.1 wbu2352 | DETP_MV55.50.1 wbu2352 | Neustrelitz | 53.3912 | 13.0444 | 100000 | 21566 | YES | 134.7875 | 431.32 | 323.49 | 646.98 | 781.7675 | 4690.605 | DE80 | C
DE | DE80J | DEAG_MV55.74.1 | DETP_MV55.74.1 | Wesenberg | 53.2751 | 12.9728 | 7450 | 6340 | NO | 39.625 | 0 | 0 | 0 | 229.825 | 1378.95 | DE80 | B
DE | DE80J | DEAG_MV55.82.1 wbu752 | DETP_MV55.82.1 wbu752 | Feldberg | 53.385 | 13.4308 | 5000 | 3230 | NO | 20.1875 | 0 | 0 | 0 | 117.0875 | 702.525 | DE80 | C
DE | DE80J | DEAG_MV56.41.1 wbu1997 | DETP_MV56.41.1 wbu1997 | Malchow | 53.4955 | 12.4196 | 20000 | 14245 | NO | 89.0312 | 0 | 0 | 0 | 516.3812 | 3098.2875 | DE80 | B
DE | DE80J | DEAG_MV56.56.1 wbu274 | DETP_MV56.56.1 wbu274 | Rechlin | 53.3179 | 12.7216 | 5000 | 2819 | NO | 17.6188 | 0 | 0 | 0 | 102.1887 | 613.1325 | DE80 | C
DE | DE80J | DEAG_MV56.57.1 wbu2000 | DETP_MV56.57.1 wbu2000 | Röbel | 53.387 | 12.5681 | 11500 | 5522 | NO | 34.5125 | 0 | 0 | 0 | 200.1725 | 1201.035 | DE80 | C
DE | DE80J | DEAG_MV56.72.1 | DETP_MV56.72.1 | Waren | 53.5464 | 12.592 | 93000 | 65692 | YES | 410.575 | 1313.84 | 985.38 | 1970.76 | 2381.335 | 14288.01 | DE80 | C
DE | DE80L | DEAG_MV57.36.2 wbu2377 | DETP_MV57.36.2 wbu2377 | Grimmen | 54.1169 | 13.026 | 26000 | 15094 | NO | 94.3375 | 0 | 0 | 0 | 547.1575 | 3282.945 | DE80 | B
DE | DE80L | DEAG_MV57.78.1 wbu2360 | DETP_MV57.78.1 wbu2360 | Kneese/Schulenberg | 54.1298 | 12.6192 | 29300 | 17623 | NO | 110.1438 | 0 | 0 | 0 | 638.8338 | 3833.0025 | DE80 | C
DE | DE80L | DEAG_MV57.91.1 wbu1573 | DETP_MV57.91.1 wbu1573 | Wieck a. Darß | 54.4209 | 12.5913 | 27200 | 8480 | NO | 53 | 0 | 0 | 0 | 307.4 | 1844.4 | DE80 | C
DE | DE80L | DEAG_MV57.96.2 wbu2139 | DETP_MV57.96.2 wbu2139 | Zingst | 54.4309 | 12.704 | 28000 | 6874 | NO | 42.9625 | 0 | 0 | 0 | 249.1825 | 1495.095 | DE80 | A
DE | DE80M | DEAG_MV58.03.1 wbu2079 | DETP_MV58.03.1 wbu2079 | Bad Kleinen | 53.7805 | 11.4942 | 6500 | 5462 | NO | 34.1375 | 0 | 0 | 0 | 197.9975 | 1187.985 | DE80 | C
DE | DE80M | DEAG_MV58.14.1 wbu2150 | DETP_MV58.14.1 wbu2150 | Boltenhagen | 53.9846 | 11.2018 | 15000 | 11911 | NO | 74.4438 | 0 | 0 | 0 | 431.7738 | 2590.6425 | DE80 | A
DE | DE80M | DEAG_MV58.17.2 wbu2351 | DETP_MV58.17.2 wbu2351 | Radegast | 53.7644 | 11.047 | 19400 | 28544 | NO | 178.4 | 0 | 0 | 0 | 1034.72 | 6208.32 | DE80 | C
DE | DE80M | DEAG_MV58.22.1 wbu2001 | DETP_MV58.22.1 wbu2001 | Dassow | 53.8962 | 10.9846 | 20000 | 15771 | NO | 98.5688 | 0 | 0 | 0 | 571.6988 | 3430.1925 | DE80 | C
DE | DE80M | DEAG_MV58.25.1 wbu1285 | DETP_MV58.25.1 wbu1285 | Dorf Mecklenburg | 53.8523 | 11.4474 | 8900 | 4471 | NO | 27.9437 | 0 | 0 | 0 | 162.0737 | 972.4425 | DE80 | B
DE | DE80M | DEAG_MV58.34.1 wbu197 | DETP_MV58.34.1 wbu197 | Grevesmühlen | 53.8694 | 11.1624 | 65000 | 43808 | YES | 273.8 | 876.16 | 657.12 | 1314.24 | 1588.04 | 9528.24 | DE80 | C
DE | DE80N | DEAG_MV59.96.1 wbu945 | DETP_MV59.96.1 wbu945 | Ückeritz | 54.0172 | 14.0322 | 27000 | 12021 | NO | 75.1313 | 0 | 0 | 0 | 435.7613 | 2614.5675 | DE80 | C
DE | DE80O | DEAG_MV60.10.1 wbu384 | DETP_MV60.10.1 wbu384 | Crivitz | 53.577 | 11.6556 | 6000 | 4258 | NO | 26.6125 | 0 | 0 | 0 | 154.3525 | 926.115 | DE80 | A
DE | DE80O | DEAG_MV60.15.1 wbu1497 | DETP_MV60.15.1 wbu1497 | Dobbertin | 53.6229 | 12.0601 | 8042 | 4117 | NO | 25.7313 | 0 | 0 | 0 | 149.2413 | 895.4475 | DE80 | A
DE | DE80L | DEAG_MV60.25.1 wbu472 | DETP_MV60.25.1 wbu472 | Göhren | 54.3363 | 13.7367 | 30000 | 12911 | NO | 80.6938 | 0 | 0 | 0 | 468.0238 | 2808.1425 | DE80 | A
DE | DE80O | DEAG_MV60.49.1 wbu1190 | DETP_MV60.49.1 wbu1190 | Lübz | 53.4525 | 12.0198 | 36500 | 17847 | NO | 111.5438 | 0 | 0 | 0 | 646.9538 | 3881.7225 | DE80 | B
DE | DE80O | DEAG_MV60.56.1 wbu277 | DETP_MV60.56.1 wbu277 | Parchim | 53.4377 | 11.8265 | 37000 | 16683 | NO | 104.2688 | 0 | 0 | 0 | 604.7587 | 3628.5525 | DE80 | B
DE | DE80O | DEAG_MV60.61.1 wbu275 | DETP_MV60.61.1 wbu275 | Plau | 53.4576 | 12.2403 | 15000 | 7357 | NO | 45.9812 | 0 | 0 | 0 | 266.6912 | 1600.1475 | DE80 | B
DE | DE80O | DEAG_MV60.73.3 wbu2033 | DETP_MV60.73.3 wbu2033 | Sternberg | 53.7361 | 11.8368 | 9800 | 3996 | NO | 24.975 | 0 | 0 | 0 | 144.855 | 869.13 | DE80 | C
DE | DE80L | DEAG_MV61.04.1 wbu512 | DETP_MV61.04.1 wbu512 | Bergen auf Rügen | 54.4151 | 13.452 | 92000 | 93762 | YES | 586.0125 | 1875.24 | 1406.43 | 2812.86 | 3398.8725 | 20393.235 | DE80 | B
DE | DE80L | DEAG_MV61.06.1 wbu2290 | DETP_MV61.06.1 wbu2290 | Breege/Lobkevitz | 54.5997 | 13.3443 | 7000 | 4672 | NO | 29.2 | 0 | 0 | 0 | 169.36 | 1016.16 | DE80 | C
DE | DE80L | DEAG_MV61.08.1 wbu1168 | DETP_MV61.08.1 wbu1168 | Dranske | 54.6356 | 13.246 | 7000 | 2637 | NOT KNOWN | 16.4812 | 0 | 0 | 0 | 95.5912 | 573.5475 | DE80 | C
DE | DE80L | DEAG_MV61.11.1 wbu160 | DETP_MV61.11.1 wbu160 | Garz | 54.3037 | 13.3474 | 8000 | 3873 | NO | 24.2063 | 0 | 0 | 0 | 140.3962 | 842.3775 | DE80 | C
DE | DE80L | DEAG_MV61.17.1 wbu408 | DETP_MV61.17.1 wbu408 | Vitte | 54.544 | 13.1138 | 7000 | 2196 | NO | 13.725 | 0 | 0 | 0 | 79.605 | 477.63 | DE80 | C
DE | DE80N | DEAG_MV62.12.1 wbu949 | DETP_MV62.12.1 wbu949 | Ueckermünde/Eggesin | 53.7 | 14.0631 | 40000 | 14291 | YES | 89.3188 | 285.82 | 214.365 | 428.73 | 518.0488 | 3108.2925 | DE80 | B
DE | DE80N | DEAG_MV62.33.1 wbu-87 | DETP_MV62.33.1 wbu-87 | Löcknitz | 53.4641 | 14.1966 | 8000 | 6337 | NO | 39.6063 | 0 | 0 | 0 | 229.7163 | 1378.2975 | DE80 | B
DE | DE80N | DEAG_MV62.43.1 wbu1013 | DETP_MV62.43.1 wbu1013 | Pasewalk | 53.5164 | 13.9948 | 15000 | 12341 | NO | 77.1313 | 0 | 0 | 0 | 447.3613 | 2684.1675 | DE80 | A
DE | DE80N | DEAG_MV62.56.1 wbu2512 | DETP_MV62.56.1 wbu2512 | Strasburg | 53.5076 | 13.7929 | 8650 | 6264 | NO | 39.15 | 0 | 0 | 0 | 227.07 | 1362.42 | DE80 | C
DE | DE80N | DEAG_MV62.58.4 wbu938 | DETP_MV62.58.4 wbu938 | Torgelow | 53.6465 | 14.0329 | 15000 | 7942 | NO | 49.6375 | 0 | 0 | 0 | 287.8975 | 1727.385 | DE80 | B
DE | DE80N | DEAG_MVwbu4261 | DETP_MVwbu4261 | Lubmin (neu) | 54.1504 | 13.6511 | 30000 | 18088 | NO | 113.05 | 0 | 0 | 0 | 655.69 | 3934.14 | DE80 | A
DE | DED2D | DEAG_SN1169 | DETP_SN1003 | ZKA Rennersdorf | 51.0307 | 14.8004 | 6500 | 4799 | NO | 29.9938 | 0 | 0 | 0 | 173.9638 | 1043.7825 | DED2 | B
DE | DED2C | DEAG_SN1133 | DETP_SN1005 | ZKA Bischofswerda | 51.1196 | 14.1678 | 20000 | 16400 | NO | 102.5 | 0 | 0 | 0 | 594.5 | 3567 | DED2 | A
DE | DED2C | DEAG_SN1141 | DETP_SN1012 | ZKA Neukirch/Lausitz Niederneukirch | 51.0963 | 14.2693 | 7000 | 5581 | NO | 34.8813 | 0 | 0 | 0 | 202.3112 | 1213.8675 | DED2 | A
DE | DED53 | DEAG_SN3135 | DETP_SN132 | Delitzsch | 51.5457 | 12.3175 | 45000 | 39980 | YES | 249.875 | 799.6 | 599.7 | 1199.4 | 1449.275 | 8695.65 | DED5 | B
DE | DED43 | DEAG_SN3299 | DETP_SN137 | Döbeln | 51.13 | 13.0636 | 41000 | 32000 | YES | 200 | 640 | 480 | 960 | 1160 | 6960 | DED4 | A
DE | DED21 |  | DETP_SN146 | KA Dresden-Kaditz | 51.071 | 13.6736 | 787000 | 682000 | YES | 4262.5 | 13640 | 10230 | 20460 | 24722.5 | 148335 | DED2 | B
DE | DED53 |  | DETP_SN151 | Eilenburg | 51.4753 | 12.6193 | 49000 | 41100 | YES | 256.875 | 822 | 616.5 | 1233 | 1489.875 | 8939.25 | DED5 | C
DE | DED52 |  | DETP_SN162 | Espenhain | 51.1924 | 12.4769 | 95000 | 70000 | YES | 437.5 | 1400 | 1050 | 2100 | 2537.5 | 15225 | DED5 | A
DE | DED43 | DEAG_SN2005 | DETP_SN170 | ZKA Frankenberg | 50.921 | 13.0304 | 40000 | 35500 | YES | 221.875 | 710 | 532.5 | 1065 | 1286.875 | 7721.25 | DED4 | A
DE | DED43 | DEAG_SN2002 | DETP_SN179 | Freiberg | 50.9421 | 13.3327 | 100000 | 73000 | YES | 456.25 | 1460 | 1095 | 2190 | 2646.25 | 15877.5 | DED4 | C
DE | DED42 |  | DETP_SN191 | Gelenau Verbandskläranlage | 50.7153 | 13.0017 | 19000 | 16200 | NO | 101.25 | 0 | 0 | 0 | 587.25 | 3523.5 | DED4 | B
DE | DED2E | DEAG_SN5005 | DETP_SN201 | GKA Großenhain | 51.2911 | 13.4857 | 28000 | 26250 | NO | 164.0625 | 0 | 0 | 0 | 951.5625 | 5709.375 | DED2 | B
DE | DED2E |  | DETP_SN202 | GKA Meißen | 51.1905 | 13.4266 | 105000 | 105000 | YES | 656.25 | 2100 | 1575 | 3150 | 3806.25 | 22837.5 | DED2 | C
DE | DED43 |  | DETP_SN2025 | Niederwiesa Gruppenklärwerk | 50.8686 | 13.0405 | 25000 | 19500 | NO | 121.875 | 0 | 0 | 0 | 706.875 | 4241.25 | DED4 | B
DE | DED42 |  | DETP_SN2043 | ZKA Thalheim | 50.712 | 12.8757 | 22000 | 17525 | NO | 109.5312 | 0 | 0 | 0 | 635.2812 | 3811.6875 | DED4 | B
DE | DED42 |  | DETP_SN2046 | ZKA Zschopau | 50.7432 | 13.0823 | 17000 | 11218 | NO | 70.1125 | 0 | 0 | 0 | 406.6525 | 2439.915 | DED4 | A
DE | DED42 | DEAG_SN2116 | DETP_SN2050 | KA Wünschendorf | 50.7433 | 13.1919 | 8000 | 4669 | NO | 29.1813 | 0 | 0 | 0 | 169.2513 | 1015.5075 | DED4 | C
DE | DED42 |  | DETP_SN2053 | ZKA Schönfeld | 50.6079 | 12.9973 | 99350 | 70558 | YES | 440.9875 | 1411.16 | 1058.37 | 2116.74 | 2557.7275 | 15346.365 | DED4 | A
DE | DED43 | DEAG_SN2128 | DETP_SN2055 | Kriebethal ZKA | 51.0508 | 13.0153 | 45000 | 43711 | YES | 273.1938 | 874.22 | 655.665 | 1311.33 | 1584.5237 | 9507.1425 | DED4 | A
DE | DED2E | DEAG_SN5048 | DETP_SN226 | Gröditz | 51.4245 | 13.4485 | 20000 | 13871 | NO | 86.6938 | 0 | 0 | 0 | 502.8238 | 3016.9425 | DED2 | A
DE | DED43 | DEAG_SN2127 | DETP_SN239 | Hainichen ZKA | 50.9802 | 13.1146 | 25000 | 9850 | NO | 61.5625 | 0 | 0 | 0 | 357.0625 | 2142.375 | DED4 | A
DE | DED43 | DEAG_SN3344 | DETP_SN242 | Hartha | 51.0953 | 12.9825 | 10000 | 8500 | NO | 53.125 | 0 | 0 | 0 | 308.125 | 1848.75 | DED4 | A
DE | DED42 | DEAG_SN2138 | DETP_SN28002 | ZKA Thalheim 3. AS | 50.712 | 12.8757 | 9000 | 8003 | NO | 50.0188 | 0 | 0 | 0 | 290.1088 | 1740.6525 | DED4 | B
DE | DED53 | DEAG_SN3341 | DETP_SN3009 | Mügeln | 51.2375 | 13.0753 | 6000 | 5500 | NO | 34.375 | 0 | 0 | 0 | 199.375 | 1196.25 | DED5 | A
DE | DED53 | DEAG_SN3353 | DETP_SN3010 | Gotha | 51.4217 | 12.6502 | 10000 | 8230 | NO | 51.4375 | 0 | 0 | 0 | 298.3375 | 1790.025 | DED5 | C
DE | DED52 | DEAG_SN3370 | DETP_SN3015 | Geithain | 51.0528 | 12.675 | 14000 | 8935 | NO | 55.8438 | 0 | 0 | 0 | 323.8938 | 1943.3625 | DED5 | B
DE | DED52 | DEAG_SN3017 | DETP_SN3016 | Grimma | 51.2495 | 12.7514 | 25000 | 19143 | NO | 119.6438 | 0 | 0 | 0 | 693.9338 | 4163.6025 | DED5 | B
DE | DED52 |  | DETP_SN3038 | Panitzsch VKA | 51.3529 | 12.5274 | 55000 | 54325 | YES | 339.5312 | 1086.5 | 814.875 | 1629.75 | 1969.2812 | 11815.6875 | DED5 | B
DE | DED52 | DEAG_SN3363 | DETP_SN3091 | Colditz An der Eule | 51.1454 | 12.795 | 5500 | 5403 | NO | 33.7688 | 0 | 0 | 0 | 195.8588 | 1175.1525 | DED5 | B
DE | DED2F | DEAG_SN5066 | DETP_SN420 | Kreischa | 50.9611 | 13.7773 | 11500 | 10060 | NO | 62.875 | 0 | 0 | 0 | 364.675 | 2188.05 | DED2 | B
DE | DED42 | DEAG_SN4134 | DETP_SN4203 | ZKA Johanngeorgenstadt "Am Bahnhof" | 50.4407 | 12.7278 | 7500 | 4816 | NO | 30.1 | 0 | 0 | 0 | 174.58 | 1047.48 | DED4 | A
DE | DED53 | DEAG_SN3406 | DETP_SN429 | Langenreichenbach | 51.5063 | 12.8976 | 16000 | 10950 | NO | 68.4375 | 0 | 0 | 0 | 396.9375 | 2381.625 | DED5 | C
DE | DED53 | DEAG_SN3338 | DETP_SN43 | Belgern | 51.4709 | 13.1434 | 6250 | 2996 | NO | 18.725 | 0 | 0 | 0 | 108.605 | 651.63 | DED5 | C
DE | DED43 | DEAG_SN3346 | DETP_SN433 | Leisnig | 51.158 | 12.9534 | 9500 | 5713 | NO | 35.7063 | 0 | 0 | 0 | 207.0963 | 1242.5775 | DED4 | B
DE | DED52 |  | DETP_SN44 | Benndorf | 51.071 | 12.5281 | 12600 | 8040 | NO | 50.25 | 0 | 0 | 0 | 291.45 | 1748.7 | DED5 | B
DE | DED43 | DEAG_SN2105 | DETP_SN440 | Lichtenberg/Weigmannsdorf | 50.8523 | 13.3951 | 15400 | 9000 | NO | 56.25 | 0 | 0 | 0 | 326.25 | 1957.5 | DED4 | C
DE | DED2F | DEAG_SN5057 | DETP_SN447 | Lohmen | 50.9941 | 13.9802 | 5500 | 3086 | NO | 19.2875 | 0 | 0 | 0 | 111.8675 | 671.205 | DED2 | A
DE | DED52 | DEAG_SN3604 | DETP_SN45 | Bennewitz | 51.3644 | 12.7095 | 6000 | 4457 | NO | 27.8563 | 0 | 0 | 0 | 161.5663 | 969.3975 | DED5 | B
DE | DED43 | DEAG_SN2129 | DETP_SN454 | Lunzenau | 50.9733 | 12.7616 | 6500 | 5000 | NO | 31.25 | 0 | 0 | 0 | 181.25 | 1087.5 | DED4 | B
DE | DED42 | DEAG_SN2117 | DETP_SN459 | Marienberg/Hüttengrund | 50.6553 | 13.179 | 17000 | 12850 | NO | 80.3125 | 0 | 0 | 0 | 465.8125 | 2794.875 | DED4 | B
DE | DED52 | DEAG_SN3163 | DETP_SN460 | Markkleeberg | 51.2936 | 12.3554 | 30000 | 32252 | NO | 201.575 | 0 | 0 | 0 | 1169.135 | 7014.81 | DED5 | A
DE | DED52 |  | DETP_SN461 | Markranstädt | 51.3032 | 12.2044 | 18000 | 18546 | NO | 115.9125 | 0 | 0 | 0 | 672.2925 | 4033.755 | DED5 | B
DE | DED43 | DEAG_SN2011 | DETP_SN475 | Mittweida ZKA | 50.9874 | 12.9923 | 24000 | 20500 | NO | 128.125 | 0 | 0 | 0 | 743.125 | 4458.75 | DED4 | A
DE | DED42 |  | DETP_SN500 | ZKA Niederdorf | 50.742 | 12.7941 | 34000 | 27603 | NO | 172.5187 | 0 | 0 | 0 | 1000.6087 | 6003.6525 | DED4 | C
DE | DED45 | DEAG_SN2009 | DETP_SN501 | ZKA Niederfrohna Limbacher Str | 50.8774 | 12.748 | 40000 | 30388 | YES | 189.925 | 607.76 | 455.82 | 911.64 | 1101.565 | 6609.39 | DED4 | A
DE | DED2E | DEAG_SN5041 | DETP_SN5022 | Nossen | 51.0622 | 13.2859 | 8500 | 7346 | NO | 45.9125 | 0 | 0 | 0 | 266.2925 | 1597.755 | DED2 | A
DE | DED2F | DEAG_SN5002 | DETP_SN5031 | VKA Polenz | 51.0309 | 14.1623 | 20000 | 14210 | NO | 88.8125 | 0 | 0 | 0 | 515.1125 | 3090.675 | DED2 | C
DE | DED2F | DEAG_SN5054 | DETP_SN5032 | VKA Prossen | 50.9265 | 14.1296 | 10500 | 8746 | NO | 54.6625 | 0 | 0 | 0 | 317.0425 | 1902.255 | DED2 | A
DE | DED2E |  | DETP_SN512 | Nünchritz | 51.3076 | 13.3549 | 12000 | 11160 | NO | 69.75 | 0 | 0 | 0 | 404.55 | 2427.3 | DED2 | C
DE | DED2F | DEAG_SN5106 | DETP_SN522 | Rabenau | 50.9636 | 13.6374 | 6500 | 5980 | NO | 37.375 | 0 | 0 | 0 | 216.775 | 1300.65 | DED2 | B
DE | DED42 | DEAG_SN2013 | DETP_SN525 | Olbernhau | 50.6683 | 13.3092 | 18500 | 18500 | NO | 115.625 | 0 | 0 | 0 | 670.625 | 4023.75 | DED4 | B
DE | DED53 | DEAG_SN3140 | DETP_SN527 | Oschatz | 51.3139 | 13.1222 | 26000 | 25900 | NO | 161.875 | 0 | 0 | 0 | 938.875 | 5633.25 | DED5 | A
DE | DED2C | DEAG_SN1150 | DETP_SN531 | ZKA Bernsdorf | 51.3766 | 14.0702 | 6500 | 4294 | NO | 26.8375 | 0 | 0 | 0 | 155.6575 | 933.945 | DED2 | A
DE | DED43 | DEAG_SN2131 | DETP_SN544 | Penig | 50.9281 | 12.7189 | 9000 | 18900 | NO | 118.125 | 0 | 0 | 0 | 685.125 | 4110.75 | DED4 | B
DE | DED2E |  | DETP_SN586 | KA Riesa | 51.3241 | 13.291 | 97000 | 71167 | YES | 444.7938 | 1423.34 | 1067.505 | 2135.01 | 2579.8038 | 15478.8225 | DED2 | A
DE | DED43 | DEAG_SN2132 | DETP_SN588 | Rochlitz | 51.0588 | 12.7944 | 8000 | 5618 | NO | 35.1125 | 0 | 0 | 0 | 203.6525 | 1221.915 | DED4 | A
DE | DED51 |  | DETP_SN591 | Rosental | 51.3582 | 12.3363 | 550000 | 681212 | YES | 4257.575 | 13624.24 | 10218.18 | 20436.36 | 24693.935 | 148163.61 | DED5 | A
DE | DED43 | DEAG_SN3347 | DETP_SN594 | Roßwein | 51.0705 | 13.1618 | 15300 | 9200 | NO | 57.5 | 0 | 0 | 0 | 333.5 | 2001 | DED4 | B
DE | DED43 | DEAG_SN2099 | DETP_SN61 | Brand-Erbisdorf/St.Michaelis | 50.8736 | 13.2852 | 18000 | 13700 | NO | 85.625 | 0 | 0 | 0 | 496.625 | 2979.75 | DED4 | A
DE | DED2F | DEAG_SN5059 | DETP_SN619 | Sebnitz | 50.966 | 14.2272 | 12500 | 12007 | NO | 75.0438 | 0 | 0 | 0 | 435.2537 | 2611.5225 | DED2 | C
DE | DED43 | DEAG_SN2110 | DETP_SN629 | Siebenlehn | 51.0342 | 13.3191 | 10000 | 8500 | NO | 53.125 | 0 | 0 | 0 | 308.125 | 1848.75 | DED4 | B
DE | DED53 |  | DETP_SN643 | Taucha | 51.3951 | 12.4839 | 18000 | 15894 | NO | 99.3375 | 0 | 0 | 0 | 576.1575 | 3456.945 | DED5 | B
DE | DED43 | DEAG_SN2108 | DETP_SN65 | Breitenau/Oederan | 50.8425 | 13.1252 | 15000 | 10000 | NO | 62.5 | 0 | 0 | 0 | 362.5 | 2175 | DED4 | C
DE | DED53 |  | DETP_SN655 | Torgau | 51.5617 | 13.0075 | 49000 | 37600 | YES | 235 | 752 | 564 | 1128 | 1363 | 8178 | DED5 | A
DE | DED52 |  | DETP_SN657 | Trebsen | 51.2884 | 12.7609 | 6000 | 4936 | NO | 30.85 | 0 | 0 | 0 | 178.93 | 1073.58 | DED5 | A
DE | DED43 | DEAG_SN3345 | DETP_SN665 | Waldheim | 51.0804 | 13.0162 | 12000 | 11912 | NO | 74.45 | 0 | 0 | 0 | 431.81 | 2590.86 | DED4 | B
DE | DED45 |  | DETP_SN668 | ZKA Weidensdorf | 50.846 | 12.5551 | 99500 | 94281 | YES | 589.2563 | 1885.62 | 1414.215 | 2828.43 | 3417.6862 | 20506.1175 | DED4 | B
DE | DED2E |  | DETP_SN677 | Wilde Sau | 51.0624 | 13.5266 | 20000 | 19104 | NO | 119.4 | 0 | 0 | 0 | 692.52 | 4155.12 | DED2 | A
DE | DED43 |  | DETP_SN68 | Burgstädt-Heiersdorf | 50.9428 | 12.7727 | 36000 | 31000 | NO | 193.75 | 0 | 0 | 0 | 1123.75 | 6742.5 | DED4 | C
DE | DED52 | DEAG_SN3244 | DETP_SN685 | Wurzen | 51.3793 | 12.7166 | 24000 | 18000 | NO | 112.5 | 0 | 0 | 0 | 652.5 | 3915 | DED5 | B
DE | DED2C |  | DETP_SN692 | ZKA Bautzen | 51.1766 | 14.4657 | 75000 | 68120 | YES | 425.75 | 1362.4 | 1021.8 | 2043.6 | 2469.35 | 14816.1 | DED2 | B
DE | DED2D | DEAG_SN1002 | DETP_SN697 | ZKA Ebersbach | 51.0174 | 14.5709 | 33000 | 18706 | NO | 116.9125 | 0 | 0 | 0 | 678.0925 | 4068.555 | DED2 | A
DE | DED2D |  | DETP_SN701 | ZKA Großschweidnitz | 51.0658 | 14.6587 | 10000 | 8219 | NO | 51.3688 | 0 | 0 | 0 | 297.9388 | 1787.6325 | DED2 | C
DE | DED2C |  | DETP_SN706 | ZKA Hoyerswerda | 51.4758 | 14.1988 | 91500 | 56257 | YES | 351.6062 | 1125.14 | 843.855 | 1687.71 | 2039.3162 | 12235.8975 | DED2 | A
DE | DED2C | DEAG_SN1004 | DETP_SN707 | ZKA Kamenz | 51.2896 | 14.1352 | 27000 | 26934 | NO | 168.3375 | 0 | 0 | 0 | 976.3575 | 5858.145 | DED2 | B
DE | DED2C | DEAG_SN1154 | DETP_SN710 | ZKA Königsbrück | 51.2769 | 13.8781 | 9000 | 6942 | NO | 43.3875 | 0 | 0 | 0 | 251.6475 | 1509.885 | DED2 | B
DE | DED2F | DEAG_SN5061 | DETP_SN711 | ZKA Lauenstein | 50.7934 | 13.8166 | 9000 | 6846 | NO | 42.7875 | 0 | 0 | 0 | 248.1675 | 1489.005 | DED2 | C
DE | DED2D | DEAG_SN1132 | DETP_SN713 | ZKA Löbau-Nord | 51.1389 | 14.7097 | 30000 | 29860 | NO | 186.625 | 0 | 0 | 0 | 1082.425 | 6494.55 | DED2 | C
DE | DED2D |  | DETP_SN716 | ZKA Mittelherwigsdorf | 50.9252 | 14.7438 | 22000 | 19281 | NO | 120.5063 | 0 | 0 | 0 | 698.9362 | 4193.6175 | DED2 | C
DE | DED2D | DEAG_SN1183 | DETP_SN717 | ZKA Niesky | 51.2817 | 14.8503 | 29000 | 55064 | NO | 344.15 | 0 | 0 | 0 | 1996.07 | 11976.42 | DED2 | B
DE | DED2D |  | DETP_SN718 | ZKA Görlitz- Nord | 51.1691 | 15.0009 | 140000 | 87100 | YES | 544.375 | 1742 | 1306.5 | 2613 | 3157.375 | 18944.25 | DED2 | A
DE | DED2D | DEAG_SN1177 | DETP_SN719 | ZKA Ostritz | 51.0235 | 14.9388 | 5000 | 2500 | NO | 15.625 | 0 | 0 | 0 | 90.625 | 543.75 | DED2 | B
DE | DED2C |  | DETP_SN720 | ZKA Ottendorf-Okrilla | 51.1774 | 13.8122 | 26400 | 22847 | NO | 142.7938 | 0 | 0 | 0 | 828.2038 | 4969.2225 | DED2 | B
DE | DED2C |  | DETP_SN722 | ZKA Radeberg | 51.1279 | 13.9007 | 100000 | 128970 | YES | 806.0625 | 2579.4 | 1934.55 | 3869.1 | 4675.1625 | 28050.975 | DED2 | A
DE | DED2E |  | DETP_SN723 | Radeburg | 51.223 | 13.7182 | 20000 | 14551 | NO | 90.9438 | 0 | 0 | 0 | 527.4737 | 3164.8425 | DED2 | B
DE | DED2C |  | DETP_SN724 | ZKA Reichenau | 51.2579 | 13.9638 | 20000 | 17379 | NO | 108.6187 | 0 | 0 | 0 | 629.9887 | 3779.9325 | DED2 | A
DE | DED2D | DEAG_SN1184 | DETP_SN725 | ZKA Reichenbach | 51.1344 | 14.7666 | 8000 | 5403 | NO | 33.7688 | 0 | 0 | 0 | 195.8588 | 1175.1525 | DED2 | C
DE | DED2C |  | DETP_SN729 | ZKA Rodewitz | 51.1024 | 14.4479 | 45000 | 54572 | YES | 341.075 | 1091.44 | 818.58 | 1637.16 | 1978.235 | 11869.41 | DED2 | A
DE | DED2D | DEAG_SN1185 | DETP_SN730 | ZKA Rothenburg | 51.3678 | 14.9666 | 9000 | 7529 | NO | 47.0563 | 0 | 0 | 0 | 272.9262 | 1637.5575 | DED2 | B
DE | DED2F |  | DETP_SN733 | ZKA Seifersdorf | 50.9309 | 13.656 | 15000 | 15173 | NO | 94.8313 | 0 | 0 | 0 | 550.0213 | 3300.1275 | DED2 | C
DE | DED2D |  | DETP_SN736 | ZKA Weißwasser | 51.5206 | 14.6024 | 46000 | 32079 | YES | 200.4938 | 641.58 | 481.185 | 962.37 | 1162.8637 | 6977.1825 | DED2 | B
DE | DED2C | DEAG_SN1160 | DETP_SN739 | ZKA Wittichenau | 51.3942 | 14.2367 | 10000 | 9800 | NO | 61.25 | 0 | 0 | 0 | 355.25 | 2131.5 | DED2 | B
DE | DED2D |  | DETP_SN741 | ZKA Zittau | 50.894 | 14.8316 | 85000 | 84539 | YES | 528.3687 | 1690.78 | 1268.085 | 2536.17 | 3064.5387 | 18387.2325 | DED2 | A
DE | DED53 | DEAG_SN3351 | DETP_SN747 | Zschortau | 51.4865 | 12.3479 | 10000 | 6500 | NO | 40.625 | 0 | 0 | 0 | 235.625 | 1413.75 | DED5 | B
DE | DED41 |  | DETP_SN76 | Chemnitz Heinersdorf ZKA | 50.8836 | 12.892 | 400000 | 300000 | YES | 1875 | 6000 | 4500 | 9000 | 10875 | 65250 | DED4 | B
DE | DED53 | DEAG_SN3349 | DETP_SN8 | Bad Düben | 51.5949 | 12.5685 | 19000 | 12095 | NO | 75.5938 | 0 | 0 | 0 | 438.4438 | 2630.6625 | DED5 | B
DE | DEE01 | DEAG_ST151011000001 | DETP_ST151011000001 | Dessau | 51.8599 | 12.2093 | 145000 | 86346 | YES | 539.6625 | 1726.92 | 1295.19 | 2590.38 | 3130.0425 | 18780.255 | DEE0 | B
DE | DEE05 | DEAG_ST151511000001 | DETP_ST151511000001 | Zerbst | 51.9541 | 12.0247 | 86700 | 75433 | YES | 471.4563 | 1508.66 | 1131.495 | 2262.99 | 2734.4462 | 16406.6775 | DEE0 | C
DE | DEE06 | DEAG_ST151511000003 | DETP_ST151511000003 | Loburg | 52.1191 | 12.0516 | 6000 | 4158 | NO | 25.9875 | 0 | 0 | 0 | 150.7275 | 904.365 | DEE0 | C
DE | DEE0E | DEAG_ST151511000011 | DETP_ST151511000011 | Oranienbaum | 51.8156 | 12.4008 | 43000 | 42468 | YES | 265.425 | 849.36 | 637.02 | 1274.04 | 1539.465 | 9236.79 | DEE0 | C
DE | DEE0E | DEAG_ST151511000024 | DETP_ST151511000024 | Coswig | 51.8781 | 12.4276 | 20000 | 14554 | NO | 90.9625 | 0 | 0 | 0 | 527.5825 | 3165.495 | DEE0 | B
DE | DEE01 | DEAG_ST151511000031 | DETP_ST151511000031 | Impfstoffw. Tornau | 51.9004 | 12.2225 | 6900 | 3071 | NO | 19.1938 | 0 | 0 | 0 | 111.3237 | 667.9425 | DEE0 | B
DE | DEE0C | DEAG_ST151531000001 | DETP_ST151531000001 | Bernburg | 51.7998 | 11.7692 | 80000 | 65000 | YES | 406.25 | 1300 | 975 | 1950 | 2356.25 | 14137.5 | DEE0 | A
DE | DEE0C | DEAG_ST151531000010 | DETP_ST151531000010 | Crüchern | 51.7851 | 11.8681 | 5000 | 5200 | NO | 32.5 | 0 | 0 | 0 | 188.5 | 1131 | DEE0 | C
DE | DEE0C | DEAG_ST151531000011 | DETP_ST151531000011 | Könnern | 51.6688 | 11.7387 | 16000 | 11982 | NO | 74.8875 | 0 | 0 | 0 | 434.3475 | 2606.085 | DEE0 | C
DE | DEE05 | DEAG_ST151541000001 | DETP_ST151541000001 | Bitterfeld-Wolfen | 51.6517 | 12.3106 | 585833 | 584021 | YES | 3650.1313 | 11680.42 | 8760.315 | 17520.63 | 21170.7612 | 127024.5675 | DEE0 | A
DE | DEE05 | DEAG_ST151541000002 | DETP_ST151541000002 | Schlaitz | 51.6698 | 12.4229 | 9800 | 7717 | NO | 48.2312 | 0 | 0 | 0 | 279.7412 | 1678.4475 | DEE0 | C
DE | DEE05 | DEAG_ST151541000003 | DETP_ST151541000003 | Zörbig | 51.6375 | 12.0993 | 20000 | 16642 | NO | 104.0125 | 0 | 0 | 0 | 603.2725 | 3619.635 | DEE0 | C
DE | DEE05 | DEAG_ST151541000004 | DETP_ST151541000004 | Raguhn | 51.7372 | 12.301 | 12500 | 10625 | NO | 66.4062 | 0 | 0 | 0 | 385.1562 | 2310.9375 | DEE0 | C
DE | DEE05 | DEAG_ST151591000001 | DETP_ST151591000001 | Köthen | 51.7594 | 11.9572 | 45000 | 40272 | YES | 251.7 | 805.44 | 604.08 | 1208.16 | 1459.86 | 8759.16 | DEE0 | A
DE | DEE05 | DEAG_ST151591000002 | DETP_ST151591000002 | Aken | 51.8395 | 12.0699 | 27000 | 18482 | NO | 115.5125 | 0 | 0 | 0 | 669.9725 | 4019.835 | DEE0 | B
DE | DEE0E | DEAG_ST151711000001 | DETP_ST151711000001 | Wittenberg | 51.8616 | 12.5878 | 180000 | 79755 | YES | 498.4688 | 1595.1 | 1196.325 | 2392.65 | 2891.1188 | 17346.7125 | DEE0 | A
DE | DEE0E | DEAG_ST151711000003 | DETP_ST151711000003 | Gräfenhainichen | 51.7367 | 12.4591 | 15000 | 11978 | NO | 74.8625 | 0 | 0 | 0 | 434.2025 | 2605.215 | DEE0 | A
DE | DEE0E | DEAG_ST151711000005 | DETP_ST151711000005 | Merschwitz | 51.7389 | 12.7976 | 15000 | 9062 | NO | 56.6375 | 0 | 0 | 0 | 328.4975 | 1970.985 | DEE0 | C
DE | DEE0E | DEAG_ST151711000022 | DETP_ST151711000022 | Annaburg | 51.7461 | 13.0265 | 5000 | 3887 | NO | 24.2938 | 0 | 0 | 0 | 140.9038 | 845.4225 | DEE0 | C
DE | DEE0E | DEAG_ST151711000024 | DETP_ST151711000024 | Jessen | 51.7932 | 12.9297 | 67667 | 52221 | YES | 326.3813 | 1044.42 | 783.315 | 1566.63 | 1893.0113 | 11358.0675 | DEE0 | B
DE | DEE02 | DEAG_ST152021000001 | DETP_ST152021000001 | Halle-Nord | 51.5245 | 11.9207 | 300000 | 301975 | YES | 1887.3438 | 6039.5 | 4529.625 | 9059.25 | 10946.5938 | 65679.5625 | DEE0 | B
DE | DEE08 | DEAG_ST152561000002 | DETP_ST152561000002 | Naumburg | 51.1619 | 11.8317 | 65000 | 33591 | YES | 209.9438 | 671.82 | 503.865 | 1007.73 | 1217.6737 | 7306.0425 | DEE0 | B
DE | DEE08 | DEAG_ST152561000004 | DETP_ST152561000004 | Göbitz | 51.0801 | 12.1899 | 65000 | 40428 | YES | 252.675 | 808.56 | 606.42 | 1212.84 | 1465.515 | 8793.09 | DEE0 | A
DE | DEE08 | DEAG_ST152561000005 | DETP_ST152561000005 | Karsdorf | 51.2728 | 11.6517 | 51500 | 43623 | YES | 272.6438 | 872.46 | 654.345 | 1308.69 | 1581.3338 | 9488.0025 | DEE0 | A
DE | DEE08 | DEAG_ST152561000006 | DETP_ST152561000006 | Laucha | 51.2477 | 11.6502 | 37000 | 23718 | NO | 148.2375 | 0 | 0 | 0 | 859.7775 | 5158.665 | DEE0 | B
DE | DEE08 | DEAG_ST152561000007 | DETP_ST152561000007 | Freyburg | 51.1971 | 11.7767 | 45000 | 43610 | YES | 272.5625 | 872.2 | 654.15 | 1308.3 | 1580.8625 | 9485.175 | DEE0 | C
DE | DEE08 | DEAG_ST152561000031 | DETP_ST152561000031 | Bad Kösen | 51.1462 | 11.728 | 6000 | 5918 | NO | 36.9875 | 0 | 0 | 0 | 214.5275 | 1287.165 | DEE0 | B
DE | DEE0B | DEAG_ST152601000004 | DETP_ST152601000004 | Rollsdorf | 51.4856 | 11.7402 | 65000 | 54575 | YES | 341.0938 | 1091.5 | 818.625 | 1637.25 | 1978.3438 | 11870.0625 | DEE0 | C
DE | DEE0A | DEAG_ST152601000018 | DETP_ST152601000018 | Freist | 51.6124 | 11.7185 | 14100 | 13027 | NO | 81.4188 | 0 | 0 | 0 | 472.2287 | 2833.3725 | DEE0 | C
DE | DEE0A | DEAG_ST152601000019 | DETP_ST152601000019 | Hettstedt | 51.662 | 11.5255 | 30000 | 27548 | NO | 172.175 | 0 | 0 | 0 | 998.615 | 5991.69 | DEE0 | A
DE | DEE0C | DEAG_ST153521000014 | DETP_ST153521000014 | Staßfurt | 51.8628 | 11.6341 | 40000 | 32283 | YES | 201.7687 | 645.66 | 484.245 | 968.49 | 1170.2587 | 7021.5525 | DEE0 | C
DE | DEE07 | DEAG_ST153551000001 | DETP_ST153551000001 | Eilsleben | 52.1445 | 11.1949 | 10000 | 7956 | NO | 49.725 | 0 | 0 | 0 | 288.405 | 1730.43 | DEE0 | B
DE | DEE07 | DEAG_ST153551000002 | DETP_ST153551000002 | Oschersleben | 52.022 | 11.2409 | 46000 | 31682 | YES | 198.0125 | 633.64 | 475.23 | 950.46 | 1148.4725 | 6890.835 | DEE0 | B
DE | DEE07 | DEAG_ST153551000003 | DETP_ST153551000003 | Wanzleben | 52.0513 | 11.4485 | 17500 | 14961 | NO | 93.5063 | 0 | 0 | 0 | 542.3363 | 3254.0175 | DEE0 | A
DE | DEE09 | DEAG_ST153571000001 | DETP_ST153571000001 | Osterwieck | 51.9752 | 10.698 | 12800 | 10000 | NO | 62.5 | 0 | 0 | 0 | 362.5 | 2175 | DEE0 | A
DE | DEE09 | DEAG_ST153571000002 | DETP_ST153571000002 | Dedeleben | 52.0367 | 10.8892 | 10000 | 7432 | NO | 46.45 | 0 | 0 | 0 | 269.41 | 1616.46 | DEE0 | A
DE | DEE09 | DEAG_ST153571000003 | DETP_ST153571000003 | Halberstadt | 51.9008 | 11.0643 | 60000 | 58037 | YES | 362.7312 | 1160.74 | 870.555 | 1741.11 | 2103.8412 | 12623.0475 | DEE0 | A
DE | DEE09 | DEAG_ST153571000004 | DETP_ST153571000004 | Wegeleben | 51.8981 | 11.1864 | 35000 | 27532 | NO | 172.075 | 0 | 0 | 0 | 998.035 | 5988.21 | DEE0 | A
DE | DEE06 | DEAG_ST153581000001 | DETP_ST153581000001 | MD-Gerwisch | 52.1839 | 11.7339 | 426000 | 271215 | YES | 1695.0938 | 5424.3 | 4068.225 | 8136.45 | 9831.5437 | 58989.2625 | DEE0 | A
DE | DEE06 | DEAG_ST153581000002 | DETP_ST153581000002 | Möckern (Gef.hof) | 52.151 | 11.9795 | 29000 | 17038 | NO | 106.4875 | 0 | 0 | 0 | 617.6275 | 3705.765 | DEE0 | C
DE | DEE06 | DEAG_ST153581000003 | DETP_ST153581000003 | Burg-Blumenthal | 52.3266 | 11.8467 | 40000 | 36325 | YES | 227.0312 | 726.5 | 544.875 | 1089.75 | 1316.7812 | 7900.6875 | DEE0 | C
DE | DEE06 | DEAG_ST153581000004 | DETP_ST153581000004 | ReFood ARA Genthin | 52.4104 | 12.1751 | 79188 | 48046 | YES | 300.2875 | 960.92 | 720.69 | 1441.38 | 1741.6675 | 10450.005 | DEE0 | A
DE | DEE06 | DEAG_ST153581000032 | DETP_ST153581000032 | Parey | 52.3756 | 11.9427 | 9500 | 8556 | NO | 53.475 | 0 | 0 | 0 | 310.155 | 1860.93 | DEE0 | C
DE | DEE07 | DEAG_ST153621000001 | DETP_ST153621000001 | Wolmirstedt | 52.2444 | 11.641 | 23500 | 16999 | NO | 106.2437 | 0 | 0 | 0 | 616.2137 | 3697.2825 | DEE0 | A
DE | DEE07 | DEAG_ST153621000002 | DETP_ST153621000002 | Hillersleben | 52.271 | 11.5144 | 43400 | 34111 | YES | 213.1938 | 682.22 | 511.665 | 1023.33 | 1236.5238 | 7419.1425 | DEE0 | C
DE | DEE07 | DEAG_ST153621000003 | DETP_ST153621000003 | Hermsdorf | 52.1919 | 11.483 | 10000 | 9473 | NO | 59.2063 | 0 | 0 | 0 | 343.3963 | 2060.3775 | DEE0 | B
DE | DEE07 | DEAG_ST153621000005 | DETP_ST153621000005 | Calvörde | 52.3821 | 11.318 | 22500 | 14757 | NO | 92.2313 | 0 | 0 | 0 | 534.9412 | 3209.6475 | DEE0 | C
DE | DEE07 | DEAG_ST153621000007 | DETP_ST153621000007 | Oebisfelde | 52.4446 | 10.9853 | 9200 | 7506 | NO | 46.9125 | 0 | 0 | 0 | 272.0925 | 1632.555 | DEE0 | B
DE | DEE07 | DEAG_ST153621000014 | DETP_ST153621000014 | Rogätz | 52.3249 | 11.7776 | 11500 | 8939 | NO | 55.8688 | 0 | 0 | 0 | 324.0387 | 1944.2325 | DEE0 | B
DE | DEE07 | DEAG_ST153621000026 | DETP_ST153621000026 | Flechtingen | 52.3465 | 11.2458 | 6250 | 4800 | NO | 30 | 0 | 0 | 0 | 174 | 1044 | DEE0 | B
DE | DEE0D | DEAG_ST153631000001 | DETP_ST153631000001 | Bismark | 52.6533 | 11.5345 | 28000 | 18469 | NO | 115.4312 | 0 | 0 | 0 | 669.5012 | 4017.0075 | DEE0 | C
DE | DEE0D | DEAG_ST153631000002 | DETP_ST153631000002 | Kläden | 52.6253 | 11.6458 | 12000 | 8117 | NO | 50.7312 | 0 | 0 | 0 | 294.2412 | 1765.4475 | DEE0 | C
DE | DEE0D | DEAG_ST153631000004 | DETP_ST153631000004 | Stendal | 52.6103 | 11.9052 | 115000 | 106005 | YES | 662.5312 | 2120.1 | 1590.075 | 3180.15 | 3842.6813 | 23056.0875 | DEE0 | C
DE | DEE0D | DEAG_ST153631000005 | DETP_ST153631000005 | Havelberg | 52.8389 | 12.0615 | 17000 | 8052 | NO | 50.325 | 0 | 0 | 0 | 291.885 | 1751.31 | DEE0 | A
DE | DEE0D | DEAG_ST153631000008 | DETP_ST153631000008 | Seehausen | 52.8822 | 11.7563 | 6000 | 4958 | NO | 30.9875 | 0 | 0 | 0 | 179.7275 | 1078.365 | DEE0 | A
DE | DEE0D | DEAG_ST153631000015 | DETP_ST153631000015 | Osterburg | 52.7843 | 11.7613 | 10000 | 9028 | NO | 56.425 | 0 | 0 | 0 | 327.265 | 1963.59 | DEE0 | A
DE | DEE0D | DEAG_ST153631000041 | DETP_ST153631000041 | Tangermünde | 52.5354 | 11.962 | 13200 | 11984 | NO | 74.9 | 0 | 0 | 0 | 434.42 | 2606.52 | DEE0 | A
DE | DEE0D | DEAG_ST153631000043 | DETP_ST153631000043 | Lüderitz | 52.4971 | 11.7496 | 8500 | 7798 | NO | 48.7375 | 0 | 0 | 0 | 282.6775 | 1696.065 | DEE0 | B
DE | DEE09 | DEAG_ST153641000001 | DETP_ST153641000001 | Quedlinburg | 51.8048 | 11.1823 | 52000 | 39707 | YES | 248.1688 | 794.14 | 595.605 | 1191.21 | 1439.3787 | 8636.2725 | DEE0 | C
DE | DEE09 | DEAG_ST153641000002 | DETP_ST153641000002 | Thale | 51.7546 | 11.0775 | 25000 | 13795 | NO | 86.2188 | 0 | 0 | 0 | 500.0687 | 3000.4125 | DEE0 | A
DE | DEE09 | DEAG_ST153641000006 | DETP_ST153641000006 | Ballenstedt | 51.7264 | 11.2524 | 10000 | 7483 | NO | 46.7688 | 0 | 0 | 0 | 271.2588 | 1627.5525 | DEE0 | A
DE | DEE09 | DEAG_ST153641000008 | DETP_ST153641000008 | Harzgerode | 51.642 | 11.1274 | 6500 | 6000 | NO | 37.5 | 0 | 0 | 0 | 217.5 | 1305 | DEE0 | B
DE | DEE0C | DEAG_ST153671000002 | DETP_ST153671000002 | Schönebeck | 52.0289 | 11.6946 | 90000 | 57724 | YES | 360.775 | 1154.48 | 865.86 | 1731.72 | 2092.495 | 12554.97 | DEE0 | B
DE | DEE0C | DEAG_ST153671000003 | DETP_ST153671000003 | Calbe/Saale | 51.9158 | 11.8146 | 155000 | 79050 | YES | 494.0625 | 1581 | 1185.75 | 2371.5 | 2865.5625 | 17193.375 | DEE0 | B
DE | DEE09 | DEAG_ST153691000002 | DETP_ST153691000002 | Silstedt | 51.8675 | 10.861 | 80000 | 58900 | YES | 368.125 | 1178 | 883.5 | 1767 | 2135.125 | 12810.75 | DEE0 | A
DE | DEE09 | DEAG_ST153691000003 | DETP_ST153691000003 | Blankenburg | 51.785 | 10.9974 | 30000 | 25974 | NO | 162.3375 | 0 | 0 | 0 | 941.5575 | 5649.345 | DEE0 | C
DE | DEE09 | DEAG_ST153691000004 | DETP_ST153691000004 | Rübeland | 51.7501 | 10.8325 | 30000 | 27718 | NO | 173.2375 | 0 | 0 | 0 | 1004.7775 | 6028.665 | DEE0 | A
DE | DEE04 | DEAG_ST153701000001 | DETP_ST153701000001 | Mieste | 52.4664 | 11.201 | 10000 | 4984 | NO | 31.15 | 0 | 0 | 0 | 180.67 | 1084.02 | DEE0 | C
DE | DEE04 | DEAG_ST153701000002 | DETP_ST153701000002 | Gardelegen | 52.5389 | 11.3879 | 50000 | 42168 | YES | 263.55 | 843.36 | 632.52 | 1265.04 | 1528.59 | 9171.54 | DEE0 | B
DE | DEE04 | DEAG_ST153701000003 | DETP_ST153701000003 | Immekath | 52.6337 | 11.079 | 36500 | 22511 | NO | 140.6937 | 0 | 0 | 0 | 816.0237 | 4896.1425 | DEE0 | A
DE | DEE04 | DEAG_ST153701000005 | DETP_ST153701000005 | Salzwedel | 52.8719 | 11.1661 | 45000 | 26185 | YES | 163.6562 | 523.7 | 392.775 | 785.55 | 949.2062 | 5695.2375 | DEE0 | B
DE | DEE04 | DEAG_ST153701000006 | DETP_ST153701000006 | Arendsee/Thielbeer | 52.8427 | 11.4704 | 19000 | 5129 | NO | 32.0562 | 0 | 0 | 0 | 185.9262 | 1115.5575 | DEE0 | C
DE | DEZZZ | DEAG_SN2010 | DETP_SN2048 | KA Meerane (TH) | 50.8699 | 12.4572 | 24000 | 17344 | NOT KNOWN | 108.4 | 0 | 0 | 0 | 628.72 | 3772.32 | DEG0 | B
DE | DEG0G | DEAG_TH19807 | DETP_TH19807 | Blankenhain | 50.8488 | 11.3034 | 9999 | 6692 | NO | 41.825 | 0 | 0 | 0 | 242.585 | 1455.51 | DEG0 | C
DE | DEG0D | DEAG_TH20107 | DETP_TH20107 | Großneuhausen | 51.1603 | 11.2735 | 21000 | 14963 | NO | 93.5188 | 0 | 0 | 0 | 542.4088 | 3254.4525 | DEG0 | B
DE | DEG0D | DEAG_TH20787 | DETP_TH20787 | Wallichen | 51.0169 | 11.1473 | 14000 | 5093 | NO | 31.8313 | 0 | 0 | 0 | 184.6213 | 1107.7275 | DEG0 | C
DE | DEG0D | DEAG_TH20827 | DETP_TH20827 | Weißensee | 51.197 | 11.0892 | 12000 | 8198 | NO | 51.2375 | 0 | 0 | 0 | 297.1775 | 1783.065 | DEG0 | C
DE | DEG0L | DEAG_TH21729 | DETP_TH21729 | Ronneburg | 50.8579 | 12.1419 | 10000 | 6608 | NO | 41.3 | 0 | 0 | 0 | 239.54 | 1437.24 | DEG0 | B
DE | DEG0P | DEAG_TH22507 | DETP_TH22507 | Bad Liebenstein / Meimers | 50.7808 | 10.3375 | 17500 | 5912 | NO | 36.95 | 0 | 0 | 0 | 214.31 | 1285.86 | DEG0 | C
DE | DEG0P | DEAG_TH22607 | DETP_TH22607 | Gerstungen | 50.9619 | 10.0882 | 8000 | 8644 | NO | 54.025 | 0 | 0 | 0 | 313.345 | 1880.07 | DEG0 | C
DE | DEG0P | DEAG_TH30356 | DETP_TH30356 | Barchfeld | 50.8006 | 10.2884 | 12000 | 9062 | NO | 56.6375 | 0 | 0 | 0 | 328.4975 | 1970.985 | DEG0 | B
DE | DEG0B | DEAG_TH31579 | DETP_TH31579 | Viernau (Haselgrund) | 50.65 | 10.5556 | 12000 | 10173 | NO | 63.5813 | 0 | 0 | 0 | 368.7713 | 2212.6275 | DEG0 | C
DE | DEG0G | DEAG_TH42825 | DETP_TH42825 | Nohra | 50.9732 | 11.2323 | 45000 | 4322 | YES | 27.0125 | 86.44 | 64.83 | 129.66 | 156.6725 | 940.035 | DEG0 | C
DE | DEG0C | DEAG_TH43849 | DETP_TH43849 | Ernstroda | 50.8752 | 10.635 | 10800 | 12046 | NO | 75.2875 | 0 | 0 | 0 | 436.6675 | 2620.005 | DEG0 | B
DE | DEG0P | DEAG_TH45059 | DETP_TH45059 | Treffurt | 51.1302 | 10.2234 | 5000 | 3712 | NO | 23.2 | 0 | 0 | 0 | 134.56 | 807.36 | DEG0 | B
DE | DEG0E | DEAG_TH45712 | DETP_TH45712 | Eisfeld | 50.4163 | 10.8409 | 6330 | 5102 | NO | 31.8875 | 0 | 0 | 0 | 184.9475 | 1109.685 | DEG0 | C
DE | DEG0P | DEAG_TH53308 | DETP_TH53308 | Vacha | 50.8345 | 10.0123 | 7500 | 4081 | NO | 25.5062 | 0 | 0 | 0 | 147.9362 | 887.6175 | DEG0 | B
DE | DEG0I | DEAG_TH54917 | DETP_TH54917 | Lichte | 50.5482 | 11.1705 | 14000 | 11629 | NO | 72.6813 | 0 | 0 | 0 | 421.5512 | 2529.3075 | DEG0 | C
DE | DEG0M | DEAG_TH8561 | DETP_TH8561 | Altenburg | 51.0437 | 12.445 | 130000 | 119087 | YES | 744.2937 | 2381.74 | 1786.305 | 3572.61 | 4316.9037 | 25901.4225 | DEG0 | C
DE | DEG0G | DEAG_TH8562 | DETP_TH8562 | Apolda | 51.0414 | 11.5315 | 45000 | 43943 | YES | 274.6438 | 878.86 | 659.145 | 1318.29 | 1592.9337 | 9557.6025 | DEG0 | B
DE | DEG0F | DEAG_TH8581 | DETP_TH8581 | Arnstadt | 50.8904 | 10.9715 | 140000 | 62386 | YES | 389.9125 | 1247.72 | 935.79 | 1871.58 | 2261.4925 | 13568.955 | DEG0 | B
DE | DEG09 | DEAG_TH8582 | DETP_TH8582 | Bad Langensalza | 51.1233 | 10.6683 | 33000 | 30235 | NO | 188.9688 | 0 | 0 | 0 | 1096.0187 | 6576.1125 | DEG0 | A
DE | DEG0P | DEAG_TH8601 | DETP_TH8601 | Bad Salzungen | 50.8176 | 10.2101 | 46950 | 34574 | YES | 216.0875 | 691.48 | 518.61 | 1037.22 | 1253.3075 | 7519.845 | DEG0 | B
DE | DEG06 | DEAG_TH8622 | DETP_TH8622 | Bernterode | 51.4058 | 10.4838 | 15000 | 14704 | NO | 91.9 | 0 | 0 | 0 | 533.02 | 3198.12 | DEG0 | B
DE | DEG07 | DEAG_TH8641 | DETP_TH8641 | Bleicherode | 51.4449 | 10.6003 | 55000 | 23739 | NO | 148.3688 | 0 | 0 | 0 | 860.5387 | 5163.2325 | DEG0 | B
DE | DEG0N | DEAG_TH8642 | DETP_TH8642 | Eisenach | 51.0002 | 10.241 | 95000 | 76804 | YES | 480.025 | 1536.08 | 1152.06 | 2304.12 | 2784.145 | 16704.87 | DEG0 | C
DE | DEG0J | DEAG_TH8643 | DETP_TH8643 | Eisenberg | 50.965 | 11.9168 | 15000 | 16806 | NOT KNOWN | 105.0375 | 0 | 0 | 0 | 609.2175 | 3655.305 | DEG0 | C
DE | DEG01 | DEAG_TH8644 | DETP_TH8644 | Erfurt | 51.0401 | 10.9848 | 375000 | 397568 | YES | 2484.8 | 7951.36 | 5963.52 | 11927.04 | 14411.84 | 86471.04 | DEG0 | A
DE | DEG0C | DEAG_TH8645 | DETP_TH8645 | Fröttstädt | 50.9369 | 10.5652 | 15000 | 12757 | NO | 79.7313 | 0 | 0 | 0 | 462.4412 | 2774.6475 | DEG0 | B
DE | DEG02 | DEAG_TH8646 | DETP_TH8646 | Gera | 50.9208 | 12.0304 | 200000 | 155927 | YES | 974.5437 | 3118.54 | 2338.905 | 4677.81 | 5652.3538 | 33914.1225 | DEG0 | B
DE | DEG0C | DEAG_TH8647 | DETP_TH8647 | Gotha | 50.9685 | 10.6976 | 150000 | 73023 | YES | 456.3938 | 1460.46 | 1095.345 | 2190.69 | 2647.0837 | 15882.5025 | DEG0 | B
DE | DEG0L | DEAG_TH8648 | DETP_TH8648 | Greiz | 50.6835 | 12.1799 | 30000 | 22409 | NO | 140.0563 | 0 | 0 | 0 | 812.3262 | 4873.9575 | DEG0 | C
DE | DEG06 | DEAG_TH8649 | DETP_TH8649 | Heiligenstadt | 51.3724 | 10.0329 | 80000 | 60801 | YES | 380.0062 | 1216.02 | 912.015 | 1824.03 | 2204.0362 | 13224.2175 | DEG0 | C
DE | DEG0J | DEAG_TH8650 | DETP_TH8650 | Hermsdorf | 50.9008 | 11.8623 | 26000 | 17736 | NO | 110.85 | 0 | 0 | 0 | 642.93 | 3857.58 | DEG0 | A
DE | DEG0E | DEAG_TH8651 | DETP_TH8651 | Hildburghausen | 50.4384 | 10.7001 | 18000 | 21817 | NO | 136.3563 | 0 | 0 | 0 | 790.8663 | 4745.1975 | DEG0 | A
DE | DEG03 | DEAG_TH8652 | DETP_TH8652 | Jena | 50.9575 | 11.6341 | 210000 | 184991 | YES | 1156.1938 | 3699.82 | 2774.865 | 5549.73 | 6705.9238 | 40235.5425 | DEG0 | B
DE | DEG0J | DEAG_TH8653 | DETP_TH8653 | Kahla | 50.812 | 11.587 | 26700 | 11798 | NO | 73.7375 | 0 | 0 | 0 | 427.6775 | 2566.065 | DEG0 | A
DE | DEG06 | DEAG_TH8654 | DETP_TH8654 | Leinefelde | 51.3753 | 10.3361 | 20000 | 14984 | NO | 93.65 | 0 | 0 | 0 | 543.17 | 3259.02 | DEG0 | A
DE | DEG0F | DEAG_TH8655 | DETP_TH8655 | Ilmenau | 50.6779 | 10.9419 | 48000 | 39101 | YES | 244.3813 | 782.02 | 586.515 | 1173.03 | 1417.4113 | 8504.4675 | DEG0 | A
DE | DEG0B | DEAG_TH8656 | DETP_TH8656 | Meiningen | 50.5858 | 10.4078 | 34650 | 33169 | NO | 207.3063 | 0 | 0 | 0 | 1202.3763 | 7214.2575 | DEG0 | B
DE | DEG09 | DEAG_TH8657 | DETP_TH8657 | Mühlhausen | 51.2061 | 10.5017 | 57800 | 49109 | YES | 306.9313 | 982.18 | 736.635 | 1473.27 | 1780.2013 | 10681.2075 | DEG0 | A
DE | DEG0K | DEAG_TH8658 | DETP_TH8658 | Neustadt / Orla | 50.7302 | 11.7266 | 12500 | 13750 | NO | 85.9375 | 0 | 0 | 0 | 498.4375 | 2990.625 | DEG0 | B
DE | DEG07 | DEAG_TH8661 | DETP_TH8661 | Nordhausen | 51.4846 | 10.8217 | 100000 | 70742 | YES | 442.1375 | 1414.84 | 1061.13 | 2122.26 | 2564.3975 | 15386.385 | DEG0 | B
DE | DEG0C | DEAG_TH8662 | DETP_TH8662 | Ohrdruf | 50.8574 | 10.726 | 35500 | 29660 | NO | 185.375 | 0 | 0 | 0 | 1075.175 | 6451.05 | DEG0 | C
DE | DEG0K | DEAG_TH8681 | DETP_TH8681 | Pößneck | 50.71 | 11.6105 | 25000 | 21383 | NO | 133.6438 | 0 | 0 | 0 | 775.1337 | 4650.8025 | DEG0 | B
DE | DEG0I | DEAG_TH8682 | DETP_TH8682 | Rudolstadt | 50.7204 | 11.3762 | 80000 | 43671 | YES | 272.9438 | 873.42 | 655.065 | 1310.13 | 1583.0738 | 9498.4425 | DEG0 | B
DE | DEG0I | DEAG_TH8683 | DETP_TH8683 | Saalfeld | 50.6639 | 11.3606 | 53500 | 46119 | YES | 288.2438 | 922.38 | 691.785 | 1383.57 | 1671.8138 | 10030.8825 | DEG0 | A
DE | DEG0K | DEAG_TH8684 | DETP_TH8684 | Schleiz | 50.5692 | 11.7732 | 12500 | 12542 | NO | 78.3875 | 0 | 0 | 0 | 454.6475 | 2727.885 | DEG0 | C
DE | DEG0B | DEAG_TH8701 | DETP_TH8701 | Schmalkalden | 50.7154 | 10.3578 | 50000 | 50499 | YES | 315.6188 | 1009.98 | 757.485 | 1514.97 | 1830.5887 | 10983.5325 | DEG0 | B
DE | DEG0M | DEAG_TH8702 | DETP_TH8702 | Schmölln | 50.9059 | 12.3667 | 34200 | 30342 | NO | 189.6375 | 0 | 0 | 0 | 1099.8975 | 6599.385 | DEG0 | A
DE | DEG0A | DEAG_TH8721 | DETP_TH8721 | Sondershausen | 51.3595 | 10.9137 | 30000 | 26251 | NO | 164.0687 | 0 | 0 | 0 | 951.5987 | 5709.5925 | DEG0 | B
DE | DEG0D | DEAG_TH8741 | DETP_TH8741 | Sömmerda | 51.191 | 11.1268 | 22000 | 17759 | NO | 110.9937 | 0 | 0 | 0 | 643.7637 | 3862.5825 | DEG0 | C
DE | DEG0L | DEAG_TH8742 | DETP_TH8742 | Weida | 50.7852 | 12.073 | 17500 | 11205 | NO | 70.0312 | 0 | 0 | 0 | 406.1812 | 2437.0875 | DEG0 | B
DE | DEG04 | DEAG_TH8743 | DETP_TH8743 | Suhl | 50.6025 | 10.608 | 80000 | 64842 | YES | 405.2625 | 1296.84 | 972.63 | 1945.26 | 2350.5225 | 14103.135 | DEG0 | B
DE | DEG05 | DEAG_TH8744 | DETP_TH8744 | Weimar | 50.9932 | 11.3613 | 99600 | 72492 | YES | 453.075 | 1449.84 | 1087.38 | 2174.76 | 2627.835 | 15767.01 | DEG0 | A
DE | DEG0M | DEAG_TH8761 | DETP_TH8761 | Meuselwitz | 51.0509 | 12.3142 | 19190 | 13561 | NO | 84.7563 | 0 | 0 | 0 | 491.5863 | 2949.5175 | DEG0 | B
DE | DEG0H | DEAG_TH8781 | DETP_TH8781 | Sonneberg | 50.3016 | 11.1432 | 48375 | 39059 | YES | 244.1188 | 781.18 | 585.885 | 1171.77 | 1415.8888 | 8495.3325 | DEG0 | B
DE | DEG0B | DEAG_TH8801 | DETP_TH8801 | Zella-Mehlis | 50.6558 | 10.6274 | 30000 | 23688 | NO | 148.05 | 0 | 0 | 0 | 858.69 | 5152.14 | DEG0 | A
DE | DEG0L | DEAG_TH8802 | DETP_TH8802 | Zeulenroda | 50.6664 | 12.015 | 24500 | 20460 | NO | 127.875 | 0 | 0 | 0 | 741.675 | 4450.05 | DEG0 | B
DE | DEG0A | DEAG_TH9123 | DETP_TH9123 | Artern | 51.3642 | 11.2863 | 11000 | 10008 | NO | 62.55 | 0 | 0 | 0 | 362.79 | 2176.74 | DEG0 | A
DE | DEG07 | DEAG_TH9143 | DETP_TH9143 | Aumühle | 51.4453 | 10.9514 | 10000 | 6828 | NO | 42.675 | 0 | 0 | 0 | 247.515 | 1485.09 | DEG0 | C
DE | DEG0A | DEAG_TH9145 | DETP_TH9145 | Bad Frankenhausen | 51.3493 | 11.1114 | 13000 | 12036 | NO | 75.225 | 0 | 0 | 0 | 436.305 | 2617.83 | DEG0 | A
DE | DEG09 | DEAG_TH9146 | DETP_TH9146 | Bad Tennstedt | 51.149 | 10.861 | 6000 | 4376 | NO | 27.35 | 0 | 0 | 0 | 158.63 | 951.78 | DEG0 | A
DE | DEG0A | DEAG_TH9147 | DETP_TH9147 | Greußen | 51.2263 | 10.9543 | 5600 | 5748 | NO | 35.925 | 0 | 0 | 0 | 208.365 | 1250.19 | DEG0 | B
DE | DEG09 | DEAG_TH9149 | DETP_TH9149 | Großengottern | 51.1506 | 10.5843 | 15000 | 16223 | NO | 101.3938 | 0 | 0 | 0 | 588.0838 | 3528.5025 | DEG0 | C
DE | DEG09 | DEAG_TH9151 | DETP_TH9151 | Horsmar | 51.2732 | 10.4163 | 9900 | 11001 | NO | 68.7563 | 0 | 0 | 0 | 398.7862 | 2392.7175 | DEG0 | C
DE | DEG09 | DEAG_TH9164 | DETP_TH9164 | Niederdorla | 51.156 | 10.454 | 6000 | 4770 | NO | 29.8125 | 0 | 0 | 0 | 172.9125 | 1037.475 | DEG0 | A
DE | DEG0A | DEAG_TH9183 | DETP_TH9183 | Oldisleben | 51.319 | 11.1944 | 9800 | 8735 | NO | 54.5938 | 0 | 0 | 0 | 316.6437 | 1899.8625 | DEG0 | C
DE | DEG0A | DEAG_TH9184 | DETP_TH9184 | Roßleben | 51.2903 | 11.4452 | 7000 | 5465 | NO | 34.1562 | 0 | 0 | 0 | 198.1062 | 1188.6375 | DEG0 | A
DE | DEG0L | DEAG_TH9187 | DETP_TH9187 | Berga | 50.7503 | 12.1477 | 7700 | 2958 | NO | 18.4875 | 0 | 0 | 0 | 107.2275 | 643.365 | DEG0 | B
DE | DEG0I | DEAG_TH9189 | DETP_TH9189 | Köditz | 50.6746 | 11.1562 | 8500 | 7869 | NO | 49.1813 | 0 | 0 | 0 | 285.2513 | 1711.5075 | DEG0 | C
DE | DEG0K | DEAG_TH9190 | DETP_TH9190 | Lobenstein | 50.4425 | 11.6488 | 8500 | 9524 | NO | 59.525 | 0 | 0 | 0 | 345.245 | 2071.47 | DEG0 | B
DE | DEG0M | DEAG_TH9245 | DETP_TH9245 | Lucka | 51.1008 | 12.3354 | 6050 | 4750 | NO | 29.6875 | 0 | 0 | 0 | 172.1875 | 1033.125 | DEG0 | A
DE | DEG03 | DEAG_TH9247 | DETP_TH9247 | Jena-Maua | 50.8721 | 11.604 | 9750 | 7325 | NO | 45.7812 | 0 | 0 | 0 | 265.5312 | 1593.1875 | DEG0 | B
DE | DEG0J | DEAG_TH9263 | DETP_TH9263 | Stadtroda | 50.8662 | 11.7188 | 7000 | 6380 | NO | 39.875 | 0 | 0 | 0 | 231.275 | 1387.65 | DEG0 | A
DE | DEG0J | DEAG_TH9283 | DETP_TH9283 | Weißenborn | 50.9306 | 11.8814 | 5500 | 5135 | NO | 32.0938 | 0 | 0 | 0 | 186.1437 | 1116.8625 | DEG0 | B
DE | DEG0G | DEAG_TH9343 | DETP_TH9343 | Bad Berka | 50.909 | 11.2854 | 9999 | 8995 | NO | 56.2188 | 0 | 0 | 0 | 326.0687 | 1956.4125 | DEG0 | B
DE | DEG0D | DEAG_TH9423 | DETP_TH9423 | Kindelbrück | 51.2631 | 11.1035 | 5000 | 3215 | NO | 20.0938 | 0 | 0 | 0 | 116.5438 | 699.2625 | DEG0 | B
DE | DEG0G | DEAG_TH9443 | DETP_TH9443 | Kranichfeld | 50.8592 | 11.2159 | 6310 | 5107 | NO | 31.9188 | 0 | 0 | 0 | 185.1288 | 1110.7725 | DEG0 | B
DE | DEG0F | DEAG_TH9483 | DETP_TH9483 | Stadtilm | 50.7802 | 11.0982 | 6900 | 5013 | NO | 31.3313 | 0 | 0 | 0 | 181.7212 | 1090.3275 | DEG0 | A
DE | DEG0D | DEAG_TH9503 | DETP_TH9503 | Straußfurt | 51.1572 | 11.0003 | 6000 | 3365 | NO | 21.0312 | 0 | 0 | 0 | 121.9812 | 731.8875 | DEG0 | B
DE | DEG0C | DEAG_TH9523 | DETP_TH9523 | Tabarz | 50.8831 | 10.5192 | 8000 | 6906 | NO | 43.1625 | 0 | 0 | 0 | 250.3425 | 1502.055 | DEG0 | B
DE | DEG0C | DEAG_TH9543 | DETP_TH9543 | Tambach-Dietharz | 50.8067 | 10.6193 | 8000 | 5556 | NO | 34.725 | 0 | 0 | 0 | 201.405 | 1208.43 | DEG0 | B
DE | DEG0P | DEAG_TH9603 | DETP_TH9603 | Kaltennordheim | 50.6293 | 10.1477 | 7500 | 2884 | NO | 18.025 | 0 | 0 | 0 | 104.545 | 627.27 | DEG0 | B
DE | DEG09 | DEAG_TH9703 | DETP_TH9703 | Mihla | 51.0799 | 10.3324 | 6700 | 7955 | NO | 49.7188 | 0 | 0 | 0 | 288.3687 | 1730.2125 | DEG0 | A
DE | DEG0E | DEAG_TH9705 | DETP_TH9705 | Milz | 50.3745 | 10.5242 | 6500 | 6249 | NO | 39.0562 | 0 | 0 | 0 | 226.5262 | 1359.1575 | DEG0 | C
DE | DEG0E | DEAG_TH9725 | DETP_TH9725 | Schleusingen | 50.5006 | 10.7354 | 10000 | 5581 | NO | 34.8813 | 0 | 0 | 0 | 202.3112 | 1213.8675 | DEG0 | A
DE | DEG0E | DEAG_TH9743 | DETP_TH9743 | Themar | 50.5135 | 10.6065 | 6000 | 2619 | NO | 16.3688 | 0 | 0 | 0 | 94.9388 | 569.6325 | DEG0 | B
DE | DEE0B | DEAG_ST152611000001 | DETP_ST152611000001 | Raßnitz | 51.3931 | 12.0736 | 6500 | 4451 | NO | 27.8187 | 0 | 0 | 0 | 161.3487 | 968.0925 | DEE0 | B
DE | DEE0B | DEAG_ST152611000004 | DETP_ST152611000004 | Bad Dürrenberg | 51.3021 | 12.0502 | 40000 | 27815 | YES | 173.8438 | 556.3 | 417.225 | 834.45 | 1008.2938 | 6049.7625 | DEE0 | C
DE | DEE0B | DEAG_ST152611000007 | DETP_ST152611000007 | Kötschlitz | 51.3498 | 12.1616 | 10000 | 7522 | NO | 47.0125 | 0 | 0 | 0 | 272.6725 | 1636.035 | DEE0 | B
DE | DEE0B | DEAG_ST152611000030 | DETP_ST152611000030 | Braunsbedra | 51.2922 | 11.9211 | 23000 | 19106 | NO | 119.4125 | 0 | 0 | 0 | 692.5925 | 4155.555 | DEE0 | C
DE | DEE0B | DEAG_ST152611000034 | DETP_ST152611000034 | Leuna-Göhlitzsch | 51.327 | 12.0401 | 10000 | 8294 | NO | 51.8375 | 0 | 0 | 0 | 300.6575 | 1803.945 | DEE0 | B
DE | DEE0B | DEAG_ST152611000039 | DETP_ST152611000039 | DOW Schkopau | 51.4066 | 11.955 | 400000 | 97431 | YES | 608.9438 | 1948.62 | 1461.465 | 2922.93 | 3531.8737 | 21191.2425 | DEE0 | B
DE | DEE0B | DEAG_ST152651000005 | DETP_ST152651000005 | Pfützthal | 51.5522 | 11.8209 | 36800 | 31763 | NO | 198.5187 | 0 | 0 | 0 | 1151.4087 | 6908.4525 | DEE0 | C
DE | DEE0B | DEAG_ST152651000006 | DETP_ST152651000006 | Löbejün | 51.6566 | 11.8945 | 6500 | 8698 | NO | 54.3625 | 0 | 0 | 0 | 315.3025 | 1891.815 | DEE0 | C
DE | DEE0B | DEAG_ST152651000015 | DETP_ST152651000015 | Landsberg | 51.5334 | 12.1553 | 10000 | 13193 | NO | 82.4562 | 0 | 0 | 0 | 478.2462 | 2869.4775 | DEE0 | A
DE | DEE0B | DEAG_ST152651000018 | DETP_ST152651000018 | Queis/Dölbau | 51.4744 | 12.079 | 6250 | 4157 | NO | 25.9813 | 0 | 0 | 0 | 150.6913 | 904.1475 | DEE0 | B
DE | DEE0B | DEAG_ST152651000026 | DETP_ST152651000026 | Benndorf (Gröbers) | 51.4478 | 12.0908 | 10000 | 5291 | NO | 33.0688 | 0 | 0 | 0 | 191.7987 | 1150.7925 | DEE0 | C
DE | DEE0A | DEAG_ST152661000001 | DETP_ST152661000001 | Allstedt | 51.3917 | 11.3793 | 5500 | 4207 | NO | 26.2938 | 0 | 0 | 0 | 152.5037 | 915.0225 | DEE0 | C
DE | DEE0A | DEAG_ST152661000002 | DETP_ST152661000002 | Sangerhausen | 51.4711 | 11.276 | 40000 | 27222 | YES | 170.1375 | 544.44 | 408.33 | 816.66 | 986.7975 | 5920.785 | DEE0 | A
HR | HR031 | HRAG_0001003 | HRUWWTP_0001003_001 | Baška-Zarok | 44.978 | 14.7365 | 20600 | 12834 | NO | 80.2125 | 0 | 0 | 0 | 465.2325 | 2791.395 | HR03 | A
HR | HR04B | HRAG_0007003 | HRUWWTP_0007003_001 | Beli Manastir | 45.7809 | 18.6014 | 8000 | 9285 | NO | 58.0312 | 0 | 0 | 0 | 336.5812 | 2019.4875 | HR04 | B
HR | HR045 | HRAG_0004048 | HRUWWTP_0004048_001 | Križevci | 45.9912 | 16.5512 | 20300 | 9013 | NO | 56.3313 | 0 | 0 | 0 | 326.7212 | 1960.3275 | HR04 | B
HR | HR031 | HRAG_0001047 | HRUWWTP_0001047_001 | Krk | 45.0147 | 14.5612 | 20800 | 11859 | NO | 74.1188 | 0 | 0 | 0 | 429.8888 | 2579.3325 | HR03 | B
HR | HR04E | HRAG_0004051 | HRUWWTP_0004051_001 | Kutina | 45.4635 | 16.7717 | 20000 | 16107 | NO | 100.6688 | 0 | 0 | 0 | 583.8787 | 3503.2725 | HR04 | A
HR | HR032 | HRAG_0001074 | HRUWWTP_0001074_001 | Novalja-Vrtić | 44.5492 | 14.875 | 14500 | 23081 | NO | 144.2562 | 0 | 0 | 0 | 836.6862 | 5020.1175 | HR03 | C
HR | HR036 | HRAG_0001076 | HRUWWTP_0001076_001 | Novigrad Istarski | 45.3311 | 13.5503 | 33000 | 17059 | NO | 106.6187 | 0 | 0 | 0 | 618.3887 | 3710.3325 | HR03 | C
HR | HR046 | HRAG_0005057 | HRUWWTP_0005057_001 | Novo Selo na Dravi | 46.3188 | 16.4331 | 5000 | 3087 | NO | 19.2937 | 0 | 0 | 0 | 111.9038 | 671.4225 | HR04 | C
HR | HR04C | HRAG_0007071 | HRUWWTP_0007071_001 | Nuštar | 45.3383 | 18.862 | 5000 | 1212 | NO | 7.575 | 0 | 0 | 0 | 43.935 | 263.61 | HR04 | C
HR | HR04D | HRAG_0002003 | HRUWWTP_0002003_001 | Ogulin | 45.2496 | 15.2495 | 7500 | 4910 | NO | 30.6875 | 0 | 0 | 0 | 177.9875 | 1067.925 | HR04 | B
HR | HR035 | HRAG_0001079 | HRUWWTP_0001079_001 | Omiš | 43.4422 | 16.6858 | 32210 | 11745 | NO | 73.4062 | 0 | 0 | 0 | 425.7562 | 2554.5375 | HR03 | A
HR | HR031 | HRAG_0001080 | HRUWWTP_0001080_001 | Omišalj | 45.2022 | 14.5523 | 9200 | 2188 | NO | 13.675 | 0 | 0 | 0 | 79.315 | 475.89 | HR03 | A
HR | HR031 | HRAG_0001081 | HRUWWTP_0001081_001 | Opatija-Lovran-Ičići | 45.3188 | 14.2904 | 46000 | 28665 | NO | 179.1562 | 0 | 0 | 0 | 1039.1063 | 6234.6375 | HR03 | A
HR | HR037 | HRAG_0001082 | HRUWWTP_0001082_001 | Opuzen | 43.0197 | 17.547 | 9000 | 1770 | NO | 11.0625 | 0 | 0 | 0 | 64.1625 | 384.975 | HR03 | C
HR | HR037 | HRAG_0001084 | HRUWWTP_0001084_001 | Orebić | 42.9751 | 17.1591 | 10000 | 1000 | NO | 6.25 | 0 | 0 | 0 | 36.25 | 217.5 | HR03 | A
HR | HR033 | HRAG_0002011 | HRUWWTP_0002011_001 | Benkovac | 44.0259 | 15.6115 | 7000 | 5239 | NO | 32.7437 | 0 | 0 | 0 | 189.9137 | 1139.4825 | HR03 | B
HR | HR033 | HRAG_0001006 | HRUWWTP_0001006_001 | Biograd na Moru-Kumenat | 43.9214 | 15.4706 | 27325 | 26540 | NO | 165.875 | 0 | 0 | 0 | 962.075 | 5772.45 | HR03 | C
HR | HR047 | HRAG_0006008 | HRUWWTP_0006008_001 | Bjelovar | 45.8678 | 16.8225 | 65300 | 44256 | NO | 276.6 | 0 | 0 | 0 | 1604.28 | 9625.68 | HR04 | B
HR | HR042 | HRAG_0004018 | HRUWWTP_0004018_001 | Brckovljani-Božjakovina | 45.8201 | 16.3011 | 8400 | 0 | NO | 0 | 0 | 0 | 0 | 0 | 0 | HR04 | B
HR | HR036 | HRAG_0003026 | HRUWWTP_0003026_001 | Buzet | 45.4051 | 13.955 | 7200 | 5312 | NO | 33.2 | 0 | 0 | 0 | 192.56 | 1155.36 | HR03 | B
HR | HR037 | HRAG_0001015 | HRUWWTP_0001015_001 | Cavtat | 42.5763 | 18.2196 | 10000 | 2264 | NO | 14.15 | 0 | 0 | 0 | 82.07 | 492.42 | HR03 | A
HR | HR04C | HRAG_0007021 | HRUWWTP_0007021_001 | Cerna | 45.1924 | 18.712 | 6000 | 0 | NO | 0 | 0 | 0 | 0 | 0 | 0 | HR04 | C
HR | HR031 | HRAG_0001017 | HRUWWTP_0001017_001 | Cres-Kimen | 44.9583 | 14.3995 | 9928 | 9452 | NO | 59.075 | 0 | 0 | 0 | 342.635 | 2055.81 | HR03 | B
HR | HR046 | HRAG_0101339 | HRUWWTP_0101339_001 | Čakovec | 46.379 | 16.466 | 75000 | 59337 | NO | 370.8563 | 0 | 0 | 0 | 2150.9663 | 12905.7975 | HR04 | A
HR | HR047 | HRAG_0006012 | HRUWWTP_0006012_001 | Daruvar | 45.5903 | 17.2072 | 23000 | 14882 | NO | 93.0125 | 0 | 0 | 0 | 539.4725 | 3236.835 | HR04 | A
HR | HR031 | HRAG_0002163 | HRUWWTP_0002163_001 | Delnice | 45.4066 | 14.8083 | 6660 | 3684 | NO | 23.025 | 0 | 0 | 0 | 133.545 | 801.27 | HR03 | A
HR | HR04B | HRAG_0005001 | HRUWWTP_0005001_001 | Donji Miholjac | 45.7681 | 18.169 | 8000 | 8250 | NO | 51.5625 | 0 | 0 | 0 | 299.0625 | 1794.375 | HR04 | B
HR | HR034 | HRAG_0001022 | HRUWWTP_0001022_001 | Drniš | 43.8549 | 16.1655 | 5000 | 2157 | NO | 13.4813 | 0 | 0 | 0 | 78.1912 | 469.1475 | HR03 | B
HR | HR037 | HRAG_0001024 | HRUWWTP_0001024_001 | Dubrovnik | 42.6526 | 18.0672 | 50000 | 49772 | NO | 311.075 | 0 | 0 | 0 | 1804.235 | 10825.41 | HR03 | B
HR | HR045 | HRAG_0005012 | HRUWWTP_0005012_001 | Đurđevac | 46.0354 | 17.0837 | 9500 | 5392 | NO | 33.7 | 0 | 0 | 0 | 195.46 | 1172.76 | HR04 | B
HR | HR047 | HRAG_0006025 | HRUWWTP_0006025_001 | Garešnica | 45.5674 | 16.941 | 7000 | 4447 | NO | 27.7938 | 0 | 0 | 0 | 161.2037 | 967.2225 | HR04 | B
HR | HR032 | HRAG_0002186 | HRUWWTP_0002186_001 | Gospić | 44.5457 | 15.3841 | 5200 | 4256 | NO | 26.6 | 0 | 0 | 0 | 154.28 | 925.68 | HR03 | A
HR | HR047 | HRAG_0006029 | HRUWWTP_0006029_001 | Grubišno Polje | 45.6913 | 17.1409 | 5000 | 1959 | NO | 12.2438 | 0 | 0 | 0 | 71.0138 | 426.0825 | HR04 | B
HR | HR035 | HRAG_0001027 | HRUWWTP_0001027_001 | Hvar | 43.1885 | 16.427 | 25000 | 13033 | NO | 81.4562 | 0 | 0 | 0 | 472.4462 | 2834.6775 | HR03 | C
HR | HR04C | HRAG_0007060 | HRUWWTP_0007060_001 | Ilok | 45.2247 | 19.4054 | 8000 | 8101 | NO | 50.6313 | 0 | 0 | 0 | 293.6612 | 1761.9675 | HR04 | C
HR | HR035 | HRAG_0002052 | HRUWWTP_0002052_001 | Imotski | 43.4407 | 17.1997 | 10000 | 3560 | NO | 22.25 | 0 | 0 | 0 | 129.05 | 774.3 | HR03 | B
HR | HR042 | HRAG_0004037 | HRUWWTP_0004037_001 | Ivanić Grad | 45.6877 | 16.3952 | 20000 | 12934 | NO | 80.8375 | 0 | 0 | 0 | 468.8575 | 2813.145 | HR04 | C
HR | HR04C | HRAG_0007029 | HRUWWTP_0007029_001 | Ivankovo | 45.2754 | 18.6888 | 8000 | 0 | NO | 0 | 0 | 0 | 0 | 0 | 0 | HR04 | B
HR | HR04D | HRAG_0004040 | HRUWWTP_0004040_001 | Karlovac-Duga Resa | 45.4907 | 15.5869 | 98500 | 39812 | YES | 248.825 | 796.24 | 597.18 | 1194.36 | 1443.185 | 8659.11 | HR04 | B
HR | HR035 | HRAG_0001037 | HRUWWTP_0001037_001 | Kaštela-Trogir-Divulje | 43.5399 | 16.2972 | 40000 | 25518 | NO | 159.4875 | 0 | 0 | 0 | 925.0275 | 5550.165 | HR03 | B
HR | HR045 | HRAG_0005021 | HRUWWTP_0005021_001 | Koprivnica | 46.1809 | 16.8773 | 100000 | 52789 | NO | 329.9313 | 0 | 0 | 0 | 1913.6013 | 11481.6075 | HR04 | C
HR | HR036 | HRAG_0003068 | HRUWWTP_0003068_001 | Labin | 45.095 | 14.1158 | 7500 | 9527 | NO | 59.5437 | 0 | 0 | 0 | 345.3537 | 2072.1225 | HR03 | A
HR | HR049 | HRAG_0006047 | HRUWWTP_0006047_001 | Lipik Pakrac-Dobrovac | 45.4164 | 17.1266 | 13500 | 9877 | NO | 61.7312 | 0 | 0 | 0 | 358.0412 | 2148.2475 | HR04 | B
HR | HR031 | HRAG_0001061 | HRUWWTP_0001061_001 | Malinska-Njivice | 45.1497 | 14.5264 | 45000 | 16922 | NO | 105.7625 | 0 | 0 | 0 | 613.4225 | 3680.535 | HR03 | C
HR | HR037 | HRAG_0001062 | HRUWWTP_0001062_001 | Malostonski zaljev | 42.819 | 17.6859 | 30000 | 12000 | NO | 75 | 0 | 0 | 0 | 435 | 2610 | HR03 | C
HR | HR036 | HRAG_0001066 | HRUWWTP_0001066_001 | Medulin-Marlera | 44.8081 | 13.9648 | 34500 | 11123 | NO | 69.5187 | 0 | 0 | 0 | 403.2087 | 2419.2525 | HR03 | C
HR | HR04B | HRAG_0005004 | HRUWWTP_0005004_001 | Našice | 45.5058 | 18.1073 | 15000 | 12574 | NO | 78.5875 | 0 | 0 | 0 | 455.8075 | 2734.845 | HR04 | B
HR | HR035 | HRAG_0002137 | HRUWWTP_0002137_001 | Vrgorac | 43.199 | 17.3736 | 5000 | 2586 | NO | 16.1625 | 0 | 0 | 0 | 93.7425 | 562.455 | HR03 | B
HR | HR033 | HRAG_0001171 | HRUWWTP_0001171_001 | Zadar-Centar | 44.1062 | 15.2574 | 100000 | 59633 | NO | 372.7063 | 0 | 0 | 0 | 2161.6962 | 12970.1775 | HR03 | A
HR | HR041 | HRAG_0004008 | HRUWWTP_0004008_001 | Zagreb | 45.7925 | 16.0819 | 1200000 | 778863 | YES | 4867.8938 | 15577.26 | 11682.945 | 23365.89 | 28233.7837 | 169402.7025 | HR04 | A
HR | HR042 | HRAG_0004009 | HRUWWTP_0004009_001 | Zaprešić | 45.8389 | 15.8157 | 61000 | 30726 | NO | 192.0375 | 0 | 0 | 0 | 1113.8175 | 6682.905 | HR04 | B
HR | HR037 | HRAG_0001173 | HRUWWTP_0001173_001 | Zaton | 42.6919 | 18.0235 | 9800 | 2196 | NO | 13.725 | 0 | 0 | 0 | 79.605 | 477.63 | HR03 | A
HR | HR032 | HRAG_0002245 | HRUWWTP_0002245_001 | Otočac | 44.8752 | 15.2404 | 5000 | 4075 | NO | 25.4688 | 0 | 0 | 0 | 147.7188 | 886.3125 | HR03 | A
HR | HR04C | HRAG_0007034 | HRUWWTP_0007034_001 | Otok (Vinkovci) | 45.1366 | 18.9011 | 8500 | 0 | NO | 0 | 0 | 0 | 0 | 0 | 0 | HR04 | B
HR | HR033 | HRAG_0001086 | HRUWWTP_0001086_001 | Pag | 44.472 | 15.0506 | 10000 | 2652 | NO | 16.575 | 0 | 0 | 0 | 96.135 | 576.81 | HR03 | C
HR | HR036 | HRAG_0003099 | HRUWWTP_0003099_001 | Pazin | 45.2423 | 13.9267 | 7000 | 4332 | NO | 27.075 | 0 | 0 | 0 | 157.035 | 942.21 | HR03 | A
HR | HR048 | HRAG_0005118 | HRUWWTP_0005118_001 | Pitomača | 45.9519 | 17.2403 | 7500 | 1938 | NO | 12.1125 | 0 | 0 | 0 | 70.2525 | 421.515 | HR04 | B
HR | HR046 | HRAG_0005060 | HRUWWTP_0005060_001 | Podturen | 46.4642 | 16.5561 | 5900 | 610 | NO | 3.8125 | 0 | 0 | 0 | 22.1125 | 132.675 | HR04 | B
HR | HR04C | HRAG_0007053 | HRUWWTP_0007053_001 | Županja | 45.0678 | 18.6793 | 17000 | 12570 | NO | 78.5625 | 0 | 0 | 0 | 455.6625 | 2733.975 | HR04 | B
HR | HR049 | HRAG_0006064 | HRUWWTP_0006064_001 | Požega | 45.3363 | 17.7101 | 33500 | 25438 | NO | 158.9875 | 0 | 0 | 0 | 922.1275 | 5532.765 | HR04 | A
HR | HR036 | HRAG_0001101 | HRUWWTP_0001101_001 | Premantura | 44.7956 | 13.904 | 8400 | 4403 | NO | 27.5188 | 0 | 0 | 0 | 159.6087 | 957.6525 | HR03 | B
HR | HR036 | HRAG_0001107 | HRUWWTP_0001107_001 | Pula Centar-Valkane | 44.8545 | 13.8276 | 35000 | 78042 | NO | 487.7625 | 0 | 0 | 0 | 2829.0225 | 16974.135 | HR03 | B
HR | HR036 | HRAG_0001108 | HRUWWTP_0001108_001 | Pula Sjever-Peroj | 44.9588 | 13.7901 | 14000 | 31950 | NO | 199.6875 | 0 | 0 | 0 | 1158.1875 | 6949.125 | HR03 | C
HR | HR031 | HRAG_0001109 | HRUWWTP_0001109_001 | Punat | 45.0086 | 14.6258 | 19200 | 8471 | NO | 52.9438 | 0 | 0 | 0 | 307.0738 | 1842.4425 | HR03 | B
HR | HR036 | HRAG_0101105 | HRUWWTP_0101105_001 | Rovinj-Kuvi | 45.0684 | 13.6441 | 64900 | 57946 | NO | 362.1625 | 0 | 0 | 0 | 2100.5425 | 12603.255 | HR03 | B
HR | HR042 | HRAG_0004002 | HRUWWTP_0004002_001 | Rugvica | 45.7318 | 16.2269 | 25000 | 4256 | NO | 26.6 | 0 | 0 | 0 | 154.28 | 925.68 | HR04 | C
HR | HR032 | HRAG_0001123 | HRUWWTP_0001123_001 | Senj | 44.9849 | 14.9032 | 9900 | 6450 | NO | 40.3125 | 0 | 0 | 0 | 233.8125 | 1402.875 | HR03 | A
HR | HR035 | HRAG_0001126 | HRUWWTP_0001126_001 | Sinj | 43.6954 | 16.6532 | 30000 | 9790 | NO | 61.1875 | 0 | 0 | 0 | 354.8875 | 2129.325 | HR03 | A
HR | HR04E | HRAG_0004071 | HRUWWTP_0004071_001 | Sisak | 45.4472 | 16.4158 | 60000 | 29400 | NO | 183.75 | 0 | 0 | 0 | 1065.75 | 6394.5 | HR04 | B
HR | HR04A | HRAG_0006077 | HRUWWTP_0006077_001 | Slavonski Brod | 45.1415 | 18.0413 | 80000 | 60635 | YES | 378.9688 | 1212.7 | 909.525 | 1819.05 | 2198.0188 | 13188.1125 | HR04 | B
HR | HR035 | HRAG_0001131 | HRUWWTP_0001131_001 | Split-Solin-Stupe | 43.5194 | 16.525 | 135000 | 43147 | NO | 269.6687 | 0 | 0 | 0 | 1564.0787 | 9384.4725 | HR03 | A
HR | HR048 | HRAG_0005128 | HRUWWTP_0005128_001 | Suhopolje | 45.8112 | 17.5041 | 9900 | 1113 | NO | 6.9563 | 0 | 0 | 0 | 40.3462 | 242.0775 | HR04 | B
HR | HR031 | HRAG_0001142 | HRUWWTP_0001142_001 | Supetarska Draga | 44.8017 | 14.705 | 9995 | 4022 | NO | 25.1375 | 0 | 0 | 0 | 145.7975 | 874.785 | HR03 | C
HR | HR034 | HRAG_0001124 | HRUWWTP_0001124_001 | Šibenik | 43.7063 | 15.9007 | 50000 | 46457 | NO | 290.3562 | 0 | 0 | 0 | 1684.0662 | 10104.3975 | HR03 | B
HR | HR036 | HRAG_0001156 | HRUWWTP_0001156_001 | Umag | 45.425 | 13.5256 | 33000 | 35879 | NO | 224.2438 | 0 | 0 | 0 | 1300.6137 | 7803.6825 | HR03 | B
HR | HR044 | HRAG_0005035 | HRUWWTP_0005035_001 | Varaždin | 46.3098 | 16.3964 | 140000 | 102790 | NO | 642.4375 | 0 | 0 | 0 | 3726.1375 | 22356.825 | HR04 | C
HR | HR042 | HRAG_0004010 | HRUWWTP_0004010_001 | Velika Gorica | 45.7156 | 16.0925 | 35000 | 48048 | NO | 300.3 | 0 | 0 | 0 | 1741.74 | 10450.44 | HR04 | B
HR | HR04C | HRAG_0007050 | HRUWWTP_0007050_001 | Vinkovci-Jošine | 45.2734 | 18.8109 | 43000 | 38392 | NO | 239.95 | 0 | 0 | 0 | 1391.71 | 8350.26 | HR04 | B
HR | HR045 | HRAG_0005038 | HRUWWTP_0005038_001 | Virje | 46.0851 | 16.9975 | 5000 | 1439 | NO | 8.9938 | 0 | 0 | 0 | 52.1638 | 312.9825 | HR04 | C
HR | HR034 | HRAG_0001165 | HRUWWTP_0001165_001 | Vodice | 43.7613 | 15.7576 | 20000 | 1646 | NO | 10.2875 | 0 | 0 | 0 | 59.6675 | 358.005 | HR03 | B
IT | ITH51 |  | IT08000000000161 | RIVERGARO_PIEVE | 44.9253 | 9.6015 | 6600 | 5732 | NO | 35.825 | 0 | 0 | 0 | 207.785 | 1246.71 | ITH5 | B
IT | ITH51 |  | IT08000000000155 | MONTICELLI_D_ONGINA | 45.0808 | 9.9289 | 6250 | 4731 | NO | 29.5687 | 0 | 0 | 0 | 171.4987 | 1028.9925 | ITH5 | B
IT | ITH51 |  | IT08000000000149 | CARPANETO_PIACENTINO | 44.9236 | 9.7852 | 6800 | 5415 | NO | 33.8438 | 0 | 0 | 0 | 196.2937 | 1177.7625 | ITH5 | B
IT | ITH51 |  | IT08000000000160 | PONTENURE | 44.9992 | 9.7958 | 7000 | 5781 | NO | 36.1313 | 0 | 0 | 0 | 209.5613 | 1257.3675 | ITH5 | A
IT | ITH51 |  | IT08000000000165 | CASTELVETRO_PIACENTINO_NUOVO | 45.0705 | 10.0028 | 7000 | 5487 | NO | 34.2938 | 0 | 0 | 0 | 198.9038 | 1193.4225 | ITH5 | C
IT | ITH51 |  | IT08000000000158 | PODENZANO_CASONI | 45.0007 | 9.685 | 9200 | 8439 | NO | 52.7438 | 0 | 0 | 0 | 305.9138 | 1835.4825 | ITH5 | A
IT | ITH51 |  | IT08000000000150 | CASTELL_ARQUATO | 44.8612 | 9.8782 | 10000 | 6546 | NO | 40.9125 | 0 | 0 | 0 | 237.2925 | 1423.755 | ITH5 | B
IT | ITH55 |  | IT08000000000005 | BAZZANO | 44.5227 | 11.0822 | 14000 | 13348 | NOT KNOWN | 83.425 | 0 | 0 | 0 | 483.865 | 2903.19 | ITH5 | C
IT | ITH55 |  | IT08000000000017 | CREVALCORE | 44.7212 | 11.16 | 14000 | 9739 | NO | 60.8688 | 0 | 0 | 0 | 353.0387 | 2118.2325 | ITH5 | B
IT | ITH55 |  | IT08Q13000000007 | SAN_GIOVANNI_IN_PERSICETO_VIA_CENTESE | 44.6577 | 11.199 | 16000 | 11608 | NO | 72.55 | 0 | 0 | 0 | 420.79 | 2524.74 | ITH5 | A
IT | ITH55 |  | IT08000000000025 | MEDICINA | 44.4812 | 11.6457 | 16000 | 11841 | NO | 74.0063 | 0 | 0 | 0 | 429.2363 | 2575.4175 | ITH5 | B
IT | ITH55 |  | IT08000000000035 | SAN_GIOVANNI_IN_PERSICETO | 44.6515 | 11.1805 | 16000 | 4914 | NO | 30.7125 | 0 | 0 | 0 | 178.1325 | 1068.795 | ITH5 | B
IT | ITH55 |  | IT08000000000010 | CASTEL_DI_CASIO_PRATI | 44.1813 | 10.9875 | 18000 | 11347 | NO | 70.9188 | 0 | 0 | 0 | 411.3288 | 2467.9725 | ITH5 | A
IT | ITH54 |  | IT08000000000124 | NOVI_DI_MODENA | 44.8882 | 10.92 | 8000 | 6017 | NO | 37.6063 | 0 | 0 | 0 | 218.1162 | 1308.6975 | ITH5 | C
IT | ITH54 |  | IT08000000000106 | FIUMALBO_NUOVO | 44.1865 | 10.6465 | 9000 | 2778 | NO | 17.3625 | 0 | 0 | 0 | 100.7025 | 604.215 | ITH5 | C
IT | ITH54 |  | IT08000000000129 | SAN_FELICE_SUL_PANARO | 44.824 | 11.1551 | 9000 | 7782 | NO | 48.6375 | 0 | 0 | 0 | 282.0975 | 1692.585 | ITH5 | C
IT | ITH54 |  | IT08000000000093 | CAVEZZO | 44.8463 | 11.0224 | 10000 | 8623 | NO | 53.8938 | 0 | 0 | 0 | 312.5838 | 1875.5025 | ITH5 | B
IT | ITH54 |  | IT08000000000103 | FINALE_EMILIA | 44.8518 | 11.2872 | 10000 | 9878 | NO | 61.7375 | 0 | 0 | 0 | 358.0775 | 2148.465 | ITH5 | C
IT | ITH54 |  | IT08000000000134 | SESTOLA_FORNACE | 44.2322 | 10.7911 | 10000 | 5156 | NO | 32.225 | 0 | 0 | 0 | 186.905 | 1121.43 | ITH5 | C
IT | ITH54 |  | IT08000000000132 | SAVIGNANO_SUL_PANARO_BOCCHIROLO | 44.5029 | 11.0425 | 11000 | 9261 | NO | 57.8813 | 0 | 0 | 0 | 335.7112 | 2014.2675 | ITH5 | C
IT | ITH54 |  | IT08000000000094 | CONCORDIA_SULLA_SECCHIA | 44.9098 | 11.0015 | 13800 | 12823 | NO | 80.1437 | 0 | 0 | 0 | 464.8337 | 2789.0025 | ITH5 | B
IT | ITH54 |  | IT08000000000087 | BOMPORTO | 44.7433 | 11.0356 | 14500 | 13144 | NO | 82.15 | 0 | 0 | 0 | 476.47 | 2858.82 | ITH5 | A
IT | ITH54 |  | IT08000000000122 | NONANTOLA | 44.6811 | 11.0521 | 15000 | 12428 | NO | 77.675 | 0 | 0 | 0 | 450.515 | 2703.09 | ITH5 | B
IT | ITH54 |  | IT08000000000136 | SPILAMBERTO | 44.5678 | 10.9942 | 15000 | 11406 | NO | 71.2875 | 0 | 0 | 0 | 413.4675 | 2480.805 | ITH5 | C
IT | ITH54 |  | IT08000000000125 | PAVULLO | 44.3545 | 10.8336 | 16000 | 13330 | NO | 83.3125 | 0 | 0 | 0 | 483.2125 | 2899.275 | ITH5 | B
IT | ITH54 |  | IT08000000000112 | MIRANDOLA | 44.9005 | 11.0775 | 23000 | 22984 | NO | 143.65 | 0 | 0 | 0 | 833.17 | 4999.02 | ITH5 | A
IT | ITH54 |  | IT08000000000090 | CASTELFRANCO_EMILIA | 44.5954 | 11.0708 | 24000 | 23780 | NO | 148.625 | 0 | 0 | 0 | 862.025 | 5172.15 | ITH5 | B
IT | ITH54 |  | IT08000000000137 | VIGNOLA | 44.5051 | 11.0243 | 32000 | 32369 | NO | 202.3063 | 0 | 0 | 0 | 1173.3762 | 7040.2575 | ITH5 | B
IT | ITH54 |  | IT08000000000091 | CASTELNUOVO_RANGONE | 44.5596 | 10.9466 | 44000 | 23855 | NO | 149.0938 | 0 | 0 | 0 | 864.7437 | 5188.4625 | ITH5 | B
IT | ITH54 |  | IT08000000000131 | SASSUOLO | 44.5755 | 10.8006 | 120000 | 78251 | YES | 489.0687 | 1565.02 | 1173.765 | 2347.53 | 2836.5987 | 17019.5925 | ITH5 | A
IT | ITH54 |  | IT08000000000089 | CARPI_CORREGGIO | 44.8158 | 10.9102 | 200000 | 128643 | YES | 804.0188 | 2572.86 | 1929.645 | 3859.29 | 4663.3088 | 27979.8525 | ITH5 | A
IT | ITH54 |  | IT08000000000117 | MODENA_NAVIGLIO | 44.6768 | 10.9442 | 500000 | 246830 | YES | 1542.6875 | 4936.6 | 3702.45 | 7404.9 | 8947.5875 | 53685.525 | ITH5 | A
IT | ITH52 |  | IT08000000000175 | FIDENZA | 44.8735 | 10.0799 | 50000 | 26611 | NO | 166.3187 | 0 | 0 | 0 | 964.6487 | 5787.8925 | ITH5 | B
IT | ITH56 |  | IT08000000000081 | GORO | 44.8532 | 12.3126 | 6000 | 3152 | NO | 19.7 | 0 | 0 | 0 | 114.26 | 685.56 | ITH5 | A
IT | ITH56 |  | IT08Q13000000004 | FERRARA_GAIBANELLA_VIA_PIGNOLA | 44.7601 | 11.6678 | 6000 | 3642 | NO | 22.7625 | 0 | 0 | 0 | 132.0225 | 792.135 | ITH5 | C
IT | ITH56 |  | IT08000000000076 | POGGIO_RENATICO_NUOVO | 44.7549 | 11.5292 | 7000 | 7169 | NO | 44.8062 | 0 | 0 | 0 | 259.8762 | 1559.2575 | ITH5 | C
IT | ITH56 |  | IT08Q17000000002 | MIGLIARINO_NUOVO | 44.7368 | 11.9405 | 8000 | 4984 | NO | 31.15 | 0 | 0 | 0 | 180.67 | 1084.02 | ITH5 | C
IT | ITH55 |  | IT08000000000014 | CASTEL_SAN_PIETRO_TERME | 44.4128 | 11.5826 | 25000 | 17101 | NO | 106.8813 | 0 | 0 | 0 | 619.9112 | 3719.4675 | ITH5 | A
IT | ITH55 |  | IT08000000000004 | MINERBIO_BARICELLA | 44.638 | 11.5649 | 27000 | 18560 | NO | 116 | 0 | 0 | 0 | 672.8 | 4036.8 | ITH5 | C
IT | ITH55 |  | IT08000000000001 | ANZOLA_EMILIA | 44.5552 | 11.2025 | 30000 | 19705 | NO | 123.1562 | 0 | 0 | 0 | 714.3062 | 4285.8375 | ITH5 | C
IT | ITH55 |  | IT08000000000020 | IMOLA_SANTERNO | 44.3529 | 11.7372 | 75000 | 56361 | YES | 352.2562 | 1127.22 | 845.415 | 1690.83 | 2043.0862 | 12258.5175 | ITH5 | B
IT | ITH55 |  | IT08000000000007 | BOLOGNA_CORTICELLA | 44.5527 | 11.3621 | 800000 | 606137 | YES | 3788.3563 | 12122.74 | 9092.055 | 18184.11 | 21972.4663 | 131834.7975 | ITH5 | A
IT | ITH56 |  | IT08000000000057 | ARGENTA_OSPITAL_MONACALE | 44.6709 | 11.7185 | 5500 | 2828 | NO | 17.675 | 0 | 0 | 0 | 102.515 | 615.09 | ITH5 | C
IT | ITH56 |  | IT08000000000071 | LAGOSANTO | 44.77 | 12.1433 | 5500 | 4958 | NO | 30.9875 | 0 | 0 | 0 | 179.7275 | 1078.365 | ITH5 | A
IT | ITH56 |  | IT08000000000074 | MESOLA_BOSCO_MESOLA | 44.8813 | 12.2195 | 6000 | 5292 | NO | 33.075 | 0 | 0 | 0 | 191.835 | 1151.01 | ITH5 | B
IT | ITH52 |  | IT08000000000188 | PARMA_OVEST | 44.8244 | 10.3084 | 168000 | 108183 | YES | 676.1438 | 2163.66 | 1622.745 | 3245.49 | 3921.6338 | 23529.8025 | ITH5 | A
IT | ITH52 |  | IT08000000000187 | PARMA_EST | 44.8307 | 10.3526 | 180000 | 92360 | YES | 577.25 | 1847.2 | 1385.4 | 2770.8 | 3348.05 | 20088.3 | ITH5 | B
IT |  |  | IT210000000001 | ALTA VENOSTA | 46.7274 | 10.5349 | 30000 | 28238 | NOT KNOWN | 176.4875 | 0 | 0 | 0 | 1023.6275 | 6141.765 | ITH1 | C
IT |  |  | IT210000000003 | PRADER SAND | 46.6071 | 10.5654 | 11000 | 8376 | NOT KNOWN | 52.35 | 0 | 0 | 0 | 303.63 | 1821.78 | ITH1 | C
IT |  |  | IT210000000004 | SOLDA | 46.5187 | 10.5956 | 7500 | 6789 | NOT KNOWN | 42.4312 | 0 | 0 | 0 | 246.1012 | 1476.6075 | ITH1 | C
IT |  |  | IT210000000005 | MEDIA VENOSTA | 46.6122 | 10.8187 | 40300 | 32772 | NOT KNOWN | 204.825 | 0 | 0 | 0 | 1187.985 | 7127.91 | ITH1 | B
IT |  |  | IT210000000007 | PASSIRIA | 46.8147 | 11.2457 | 16500 | 15280 | NOT KNOWN | 95.5 | 0 | 0 | 0 | 553.9 | 3323.4 | ITH1 | A
IT |  |  | IT210000000008 | MERANO | 46.673 | 11.1476 | 364000 | 356520 | NOT KNOWN | 2228.25 | 0 | 0 | 0 | 12923.85 | 77543.1 | ITH1 | A
IT |  |  | IT210000000009 | ULTIMO | 46.5334 | 10.9616 | 5000 | 4011 | NOT KNOWN | 25.0687 | 0 | 0 | 0 | 145.3987 | 872.3925 | ITH1 | C
IT | ITH55 |  | IT08000000000015 | CASTIGLIONE_DEI_PEPOLI_CA_NOVA | 44.1506 | 11.1518 | 5000 | 3605 | NO | 22.5312 | 0 | 0 | 0 | 130.6812 | 784.0875 | ITH5 | B
IT | ITH55 |  | IT08000000000018 | GALLIERA_SAN_VENANZIO | 44.744 | 11.4464 | 8200 | 3746 | NO | 23.4125 | 0 | 0 | 0 | 135.7925 | 814.755 | ITH5 | B
IT | ITH55 |  | IT08000000000024 | MARZABOTTO | 44.3511 | 11.2102 | 5000 | 3041 | NO | 19.0063 | 0 | 0 | 0 | 110.2363 | 661.4175 | ITH5 | A
IT | ITH55 |  | IT08000000000011 | CASTEL_GUELFO | 44.4373 | 11.681 | 6000 | 3593 | NO | 22.4563 | 0 | 0 | 0 | 130.2463 | 781.4775 | ITH5 | B
IT | ITH55 |  | IT08000000000031 | PIEVE_DI_CENTO | 44.7203 | 11.3173 | 6000 | 6270 | NO | 39.1875 | 0 | 0 | 0 | 227.2875 | 1363.725 | ITH5 | B
IT | ITH55 |  | IT08000000000028 | MONTERENZIO_PIZZANO | 44.3576 | 11.4124 | 6200 | 4286 | NO | 26.7875 | 0 | 0 | 0 | 155.3675 | 932.205 | ITH5 | B
IT | ITH55 |  | IT08Q13000000002 | CASTELLO_D_ARGILE_NUOVO_MASCARINO | 44.6909 | 11.3337 | 6600 | 6180 | NO | 38.625 | 0 | 0 | 0 | 224.025 | 1344.15 | ITH5 | C
IT | ITH55 |  | IT08000000000006 | BENTIVOGLIO | 44.6516 | 11.4208 | 7000 | 4306 | NO | 26.9125 | 0 | 0 | 0 | 156.0925 | 936.555 | ITH5 | C
IT | ITH55 |  | IT08000000000026 | MOLINELLA | 44.615 | 11.6946 | 12000 | 9839 | NOT KNOWN | 61.4938 | 0 | 0 | 0 | 356.6638 | 2139.9825 | ITH5 | C
IT | ITH55 |  | IT08000000000008 | BUDRIO | 44.5457 | 11.5354 | 12000 | 10524 | NO | 65.775 | 0 | 0 | 0 | 381.495 | 2288.97 | ITH5 | B
IT | ITH55 |  | IT08000000000039 | SASSO_MARCONI | 44.3971 | 11.2629 | 12000 | 10012 | NO | 62.575 | 0 | 0 | 0 | 362.935 | 2177.61 | ITH5 | B
IT | ITH55 |  | IT08000000000016 | CRESPELLANO | 44.558 | 11.1474 | 12700 | 8725 | NO | 54.5312 | 0 | 0 | 0 | 316.2812 | 1897.6875 | ITH5 | B
IT | ITH54 |  | IT08000000000127 | RAVARINO | 44.7354 | 11.1095 | 6000 | 3191 | NO | 19.9438 | 0 | 0 | 0 | 115.6737 | 694.0425 | ITH5 | C
IT | ITH54 |  | IT08000000000109 | FORMIGINE_MAGRETA | 44.613 | 10.7913 | 6100 | 4175 | NO | 26.0938 | 0 | 0 | 0 | 151.3438 | 908.0625 | ITH5 | C
IT | ITH54 |  | IT08000000000123 | NOVI_DI_MODENA_ROVERETO | 44.8443 | 10.9467 | 6500 | 4418 | NO | 27.6125 | 0 | 0 | 0 | 160.1525 | 960.915 | ITH5 | B
IT | ITH54 |  | IT08000000000092 | CASTELVETRO_DI_MODENA | 44.5158 | 10.9533 | 7000 | 4002 | NO | 25.0125 | 0 | 0 | 0 | 145.0725 | 870.435 | ITH5 | C
IT | ITH54 |  | IT08000000000115 | MODENA_SAN_DAMASO | 44.6075 | 10.9688 | 7000 | 4347 | NO | 27.1688 | 0 | 0 | 0 | 157.5788 | 945.4725 | ITH5 | B
IT | ITH54 |  | IT08000000000128 | SAN_CESARIO_SUL_PANARO | 44.573 | 11.0328 | 7700 | 7810 | NO | 48.8125 | 0 | 0 | 0 | 283.1125 | 1698.675 | ITH5 | B
IT | ITH54 |  | IT08Q13000000009 | FANANO_NUOVO | 44.217 | 10.8079 | 7000 | 4038 | NO | 25.2375 | 0 | 0 | 0 | 146.3775 | 878.265 | ITH5 | C
IT | ITH54 |  | IT08000000000113 | MODENA_LESIGNANA | 44.6839 | 10.8975 | 8000 | 2709 | NO | 16.9313 | 0 | 0 | 0 | 98.2013 | 589.2075 | ITH5 | A
IT | ITH56 |  | IT08000000000077 | PORTOMAGGIORE | 44.6939 | 11.8216 | 14000 | 9692 | NO | 60.575 | 0 | 0 | 0 | 351.335 | 2108.01 | ITH5 | B
IT | ITH51 |  | IT08000000000148 | CAORSO | 45.0535 | 9.8713 | 5000 | 4065 | NO | 25.4062 | 0 | 0 | 0 | 147.3562 | 884.1375 | ITH5 | B
IT | ITH51 |  | IT08Q15000000001 | GRAGNANO_TREBBIENSE_NUOVO | 45.0416 | 9.5656 | 5000 | 2392 | NO | 14.95 | 0 | 0 | 0 | 86.71 | 520.26 | ITH5 | C
IT | ITH51 |  | IT08000000000143 | BOBBIO | 44.7841 | 9.4035 | 6000 | 4993 | NO | 31.2063 | 0 | 0 | 0 | 180.9963 | 1085.9775 | ITH5 | C
IT | ITH51 |  | IT08000000000152 | CORTEMAGGIORE | 45.0048 | 9.9258 | 6000 | 4518 | NO | 28.2375 | 0 | 0 | 0 | 163.7775 | 982.665 | ITH5 | C
IT | ITH56 |  | IT08000000000078 | SANT_AGOSTINO_SAN_CARLO | 44.7951 | 11.4243 | 14000 | 7973 | NO | 49.8313 | 0 | 0 | 0 | 289.0213 | 1734.1275 | ITH5 | C
IT | ITH56 |  | IT08000000000082 | TRESIGALLO_NUOVO | 44.8251 | 11.9033 | 16000 | 7328 | NO | 45.8 | 0 | 0 | 0 | 265.64 | 1593.84 | ITH5 | B
IT | ITH56 |  | IT08000000000058 | ARGENTA | 44.6237 | 11.843 | 18000 | 9143 | NO | 57.1438 | 0 | 0 | 0 | 331.4337 | 1988.6025 | ITH5 | B
IT | ITH56 |  | IT08000000000066 | COPPARO | 44.8927 | 11.8409 | 18000 | 12748 | NO | 79.675 | 0 | 0 | 0 | 462.115 | 2772.69 | ITH5 | B
IT | ITH56 |  | IT08000000000063 | CENTO | 44.753 | 11.3148 | 25000 | 25996 | NO | 162.475 | 0 | 0 | 0 | 942.355 | 5654.13 | ITH5 | B
IT | ITH53 |  | IT08000000000223 | CASALGRANDE_SALVATERRA | 44.6081 | 10.7704 | 25000 | 26990 | NO | 168.6875 | 0 | 0 | 0 | 978.3875 | 5870.325 | ITH5 | B
IT | ITH53 |  | IT08000000000236 | RUBIERA | 44.6583 | 10.7714 | 45000 | 42156 | NO | 263.475 | 0 | 0 | 0 | 1528.155 | 9168.93 | ITH5 | A
IT | ITH53 |  | IT08000000000232 | REGGIOLO_NUOVO | 44.9059 | 10.7843 | 58000 | 38095 | NO | 238.0938 | 0 | 0 | 0 | 1380.9437 | 8285.6625 | ITH5 | C
IT | ITH53 |  | IT08000000000233 | REGGIO_EMILIA_RONCOCESI | 44.7327 | 10.5578 | 150000 | 85334 | YES | 533.3375 | 1706.68 | 1280.01 | 2560.02 | 3093.3575 | 18560.145 | ITH5 | B
IT | ITH53 |  | IT08000000000234 | REGGIO_EMILIA_MANCASALE | 44.7426 | 10.6535 | 280000 | 172372 | YES | 1077.325 | 3447.44 | 2585.58 | 5171.16 | 6248.485 | 37490.91 | ITH5 | A
IT |  |  | IT210000000011 | LANA | 46.6053 | 11.1562 | 26000 | 17090 | NOT KNOWN | 106.8125 | 0 | 0 | 0 | 619.5125 | 3717.075 | ITH1 | B
IT | ITH10 |  | IT210000000016 | BOLZANO | 46.5042 | 11.3142 | 450000 | 372410 | YES | 2327.5625 | 7448.2 | 5586.15 | 11172.3 | 13499.8625 | 80999.175 | ITH1 | B
IT |  |  | IT210000000017 | WIPPTAL | 46.9081 | 11.4238 | 45000 | 45753 | NOT KNOWN | 285.9563 | 0 | 0 | 0 | 1658.5462 | 9951.2775 | ITH1 | C
IT |  |  | IT210000000018 | WASSERFELD | 46.8302 | 12.149 | 40000 | 39044 | NOT KNOWN | 244.025 | 0 | 0 | 0 | 1415.345 | 8492.07 | ITH1 | C
IT |  |  | IT210000000019 | SOMPUNT | 46.5737 | 11.8928 | 49000 | 47864 | NOT KNOWN | 299.15 | 0 | 0 | 0 | 1735.07 | 10410.42 | ITH1 | C
IT |  |  | IT210000000020 | TOBL | 46.8302 | 11.9414 | 150000 | 138050 | NOT KNOWN | 862.8125 | 0 | 0 | 0 | 5004.3125 | 30025.875 | ITH1 | B
IT |  |  | IT210000000021 | BASSA PUSTERIA | 46.8146 | 11.7412 | 40000 | 36194 | NOT KNOWN | 226.2125 | 0 | 0 | 0 | 1312.0325 | 7872.195 | ITH1 | C
IT |  |  | IT210000000023 | BRESSANONE | 46.7399 | 11.6487 | 65000 | 67776 | NOT KNOWN | 423.6 | 0 | 0 | 0 | 2456.88 | 14741.28 | ITH1 | B
IT |  |  | IT210000000025 | BASSA VALLE ISARCO | 46.6308 | 11.5492 | 45000 | 38223 | NOT KNOWN | 238.8937 | 0 | 0 | 0 | 1385.5837 | 8313.5025 | ITH1 | C
IT |  |  | IT210000000027 | PONTIVES | 46.562 | 11.7175 | 42000 | 63843 | NOT KNOWN | 399.0188 | 0 | 0 | 0 | 2314.3087 | 13885.8525 | ITH1 | B
IT |  |  | IT210000000032 | SIFFIANO | 46.5393 | 11.4603 | 6000 | 4530 | NOT KNOWN | 28.3125 | 0 | 0 | 0 | 164.2125 | 985.275 | ITH1 | A
IT |  |  | IT210000000036 | VAL D'EGA | 46.4118 | 11.5292 | 13000 | 10812 | NOT KNOWN | 67.575 | 0 | 0 | 0 | 391.935 | 2351.61 | ITH1 | C
IT |  |  | IT210000000038 | SARENTINO | 46.704 | 11.3737 | 8750 | 9989 | NOT KNOWN | 62.4313 | 0 | 0 | 0 | 362.1012 | 2172.6075 | ITH1 | C
IT |  |  | IT210000000043 | BRONZOLO | 46.4206 | 11.3511 | 342000 | 244968 | NOT KNOWN | 1531.05 | 0 | 0 | 0 | 8880.09 | 53280.54 | ITH1 | C
IT |  |  | IT210000000044 | SALORNO | 46.2429 | 11.2241 | 6000 | 4794 | NOT KNOWN | 29.9625 | 0 | 0 | 0 | 173.7825 | 1042.695 | ITH1 | B
IT |  |  | IT210000000046 | TERMENO | 46.3545 | 11.2951 | 138000 | 68945 | NOT KNOWN | 430.9062 | 0 | 0 | 0 | 2499.2562 | 14995.5375 | ITH1 | B
IT | ITH55 |  | IT08000000000021 | IMOLA_GAMBELLARA | 44.384 | 11.7299 | 30000 | 14595 | NO | 91.2188 | 0 | 0 | 0 | 529.0688 | 3174.4125 | ITH5 | A
IT | ITH55 |  | IT08000000000009 | CALDERARA_DI_RENO | 44.5702 | 11.2833 | 36000 | 16657 | NO | 104.1063 | 0 | 0 | 0 | 603.8162 | 3622.8975 | ITH5 | C
IT | ITH55 |  | IT08000000000029 | OZZANO_DELL_EMILIA_PONTE_RIZZOLI | 44.4712 | 11.4999 | 38000 | 16638 | NO | 103.9875 | 0 | 0 | 0 | 603.1275 | 3618.765 | ITH5 | B
IT | ITH59 |  | IT08000000000243 | RICCIONE | 44.0132 | 12.6346 | 180000 | 135008 | YES | 843.8 | 2700.16 | 2025.12 | 4050.24 | 4894.04 | 29364.24 | ITH5 | A
IT | ITH59 |  | IT08000000000244 | RIMINI_S_GIUSTINA | 44.0584 | 12.4959 | 560000 | 515132 | YES | 3219.575 | 10302.64 | 7726.98 | 15453.96 | 18673.535 | 112041.21 | ITH5 | A
IT | ITH56 |  | IT08000000000060 | BONDENO_CENTRO_STORICO | 44.885 | 11.4092 | 10000 | 4812 | NO | 30.075 | 0 | 0 | 0 | 174.435 | 1046.61 | ITH5 | A
IT | ITH56 |  | IT08000000000072 | MASI_SAN_GIACOMO | 44.7772 | 11.7731 | 10000 | 4245 | NO | 26.5312 | 0 | 0 | 0 | 153.8812 | 923.2875 | ITH5 | C
IT | ITH51 |  | IT08000000000159 | PONTE_DELL_OLIO | 44.8848 | 9.6629 | 12000 | 4373 | NO | 27.3313 | 0 | 0 | 0 | 158.5212 | 951.1275 | ITH5 | C
IT | ITH51 |  | IT08000000000151 | CASTEL_SAN_GIOVANNI | 45.0649 | 9.4374 | 18000 | 12182 | NO | 76.1375 | 0 | 0 | 0 | 441.5975 | 2649.585 | ITH5 | A
IT | ITH51 |  | IT08000000000147 | CALENDASCO_PONTETREBBIA | 45.0593 | 9.6348 | 16000 | 10828 | NO | 67.675 | 0 | 0 | 0 | 392.515 | 2355.09 | ITH5 | A
IT | ITH51 |  | IT08000000000144 | BORGONOVO_VAL_TIDONE | 45.0252 | 9.445 | 20000 | 6661 | NO | 41.6313 | 0 | 0 | 0 | 241.4612 | 1448.7675 | ITH5 | B
IT | ITH51 |  | IT08000000000153 | FIORENZUOLA_D_ARDA | 44.9343 | 9.9231 | 21500 | 14067 | NO | 87.9188 | 0 | 0 | 0 | 509.9287 | 3059.5725 | ITH5 | B
IT | ITH51 |  | IT08000000000156 | PIACENZA_BORGOFORTE | 45.0595 | 9.7339 | 163333 | 106886 | YES | 668.0375 | 2137.72 | 1603.29 | 3206.58 | 3874.6175 | 23247.705 | ITH5 | A
IT | ITH52 |  | IT08000000000167 | BERCETO | 44.5125 | 9.984 | 5000 | 3325 | NO | 20.7812 | 0 | 0 | 0 | 120.5312 | 723.1875 | ITH5 | A
IT | ITH52 |  | IT08000000000173 | COLORNO | 44.9291 | 10.384 | 5700 | 5543 | NO | 34.6438 | 0 | 0 | 0 | 200.9338 | 1205.6025 | ITH5 | B
IT | ITH52 |  | IT08000000000196 | TIZZANO_VAL_PARMA_LAGRIMONE | 44.4861 | 10.2479 | 6000 | 3892 | NO | 24.325 | 0 | 0 | 0 | 141.085 | 846.51 | ITH5 | C
IT | ITH52 |  | IT08000000000181 | MEDESANO | 44.7662 | 10.1443 | 6500 | 3626 | NO | 22.6625 | 0 | 0 | 0 | 131.4425 | 788.655 | ITH5 | B
IT | ITH52 |  | IT08000000000189 | SALA_BAGANZA | 44.7263 | 10.2403 | 6770 | 5308 | NO | 33.175 | 0 | 0 | 0 | 192.415 | 1154.49 | ITH5 | B
IT | ITH52 |  | IT08000000000168 | BORGO_VAL_DI_TARO | 44.4921 | 9.79 | 7500 | 6800 | NO | 42.5 | 0 | 0 | 0 | 246.5 | 1479 | ITH5 | A
IT | ITH52 |  | IT08000000000186 | PARMA_CORCAGNANO | 44.7277 | 10.3101 | 7500 | 3372 | NO | 21.075 | 0 | 0 | 0 | 122.235 | 733.41 | ITH5 | B
IT | ITH52 |  | IT08000000000192 | SAN_SECONDO_PARMENSE | 44.9228 | 10.2419 | 8000 | 4611 | NO | 28.8187 | 0 | 0 | 0 | 167.1488 | 1002.8925 | ITH5 | B
IT | ITH52 |  | IT08000000000178 | FORNOVO_DI_TARO_RICCO | 44.7049 | 10.1247 | 8300 | 5878 | NO | 36.7375 | 0 | 0 | 0 | 213.0775 | 1278.465 | ITH5 | B
IT | ITH52 |  | IT08000000000176 | FONTANELLATO | 44.8891 | 10.177 | 9000 | 7453 | NO | 46.5813 | 0 | 0 | 0 | 270.1712 | 1621.0275 | ITH5 | B
IT | ITH52 |  | IT08000000000182 | MEZZANI_MEZZANO_INFERIORE | 44.9115 | 10.4534 | 9600 | 3738 | NO | 23.3625 | 0 | 0 | 0 | 135.5025 | 813.015 | ITH5 | A
IT | ITH52 |  | IT08000000000195 | SORBOLO | 44.8499 | 10.4311 | 9900 | 8536 | NO | 53.35 | 0 | 0 | 0 | 309.43 | 1856.58 | ITH5 | B
IT | ITH52 |  | IT08000000000199 | TRAVERSETOLO | 44.6415 | 10.3888 | 9900 | 9160 | NO | 57.25 | 0 | 0 | 0 | 332.05 | 1992.3 | ITH5 | A
IT | ITH52 |  | IT08000000000184 | NOCETO | 44.82 | 10.1845 | 12000 | 6935 | NO | 43.3438 | 0 | 0 | 0 | 251.3937 | 1508.3625 | ITH5 | A
IT | ITH52 |  | IT08000000000197 | TORRILE_SAN_POLO | 44.9023 | 10.3679 | 12000 | 4892 | NO | 30.575 | 0 | 0 | 0 | 177.335 | 1064.01 | ITH5 | A
IT | ITH52 |  | IT08000000000177 | FONTEVIVO_CASE_MASSI | 44.8334 | 10.1938 | 16000 | 8826 | NO | 55.1625 | 0 | 0 | 0 | 319.9425 | 1919.655 | ITH5 | C
IT | ITH52 |  | IT08000000000171 | COLLECCHIO | 44.7578 | 10.2061 | 20000 | 13288 | NO | 83.05 | 0 | 0 | 0 | 481.69 | 2890.14 | ITH5 | A
IT | ITH52 |  | IT08000000000183 | MONTECHIARUGOLO_MONTICELLI_TERME | 44.7369 | 10.407 | 20000 | 10987 | NO | 68.6688 | 0 | 0 | 0 | 398.2788 | 2389.6725 | ITH5 | B
IT | ITH52 |  | IT08000000000180 | MEDESANO_FELEGARA | 44.7242 | 10.1236 | 22500 | 5920 | NO | 37 | 0 | 0 | 0 | 214.6 | 1287.6 | ITH5 | A
IT | ITH52 |  | IT08000000000169 | BUSSETO | 44.9885 | 10.0543 | 24000 | 12254 | NO | 76.5875 | 0 | 0 | 0 | 444.2075 | 2665.245 | ITH5 | B
IT | ITH52 |  | IT08000000000179 | LANGHIRANO | 44.6358 | 10.2751 | 25000 | 18705 | NO | 116.9062 | 0 | 0 | 0 | 678.0562 | 4068.3375 | ITH5 | B
IT | ITH52 |  | IT08000000000191 | SALSOMAGGIORE_TERME | 44.8299 | 10.0135 | 30000 | 21665 | NO | 135.4062 | 0 | 0 | 0 | 785.3562 | 4712.1375 | ITH5 | C
IT | ITH52 |  | IT08000000000174 | FELINO | 44.7001 | 10.2667 | 50000 | 21332 | NO | 133.325 | 0 | 0 | 0 | 773.285 | 4639.71 | ITH5 | C
IT | ITH53 |  | IT08000000000229 | GUASTALLA_SUD | 44.8887 | 10.6522 | 12000 | 8761 | NO | 54.7563 | 0 | 0 | 0 | 317.5863 | 1905.5175 | ITH5 | B
IT | ITH53 |  | IT08000000000237 | SAN_MARTINO_IN_RIO_NUOVO | 44.7409 | 10.7972 | 15000 | 12165 | NO | 76.0312 | 0 | 0 | 0 | 440.9812 | 2645.8875 | ITH5 | B
IT | ITH53 |  | IT08000000000231 | QUATTRO_CASTELLA_LE_FORCHE | 44.6344 | 10.5811 | 20000 | 12415 | NO | 77.5938 | 0 | 0 | 0 | 450.0437 | 2700.2625 | ITH5 | B
IT | ITH53 |  | IT08000000000225 | CASTELNOVO_DI_SOTTO_MELETOLE | 44.8544 | 10.5904 | 21000 | 18783 | NO | 117.3938 | 0 | 0 | 0 | 680.8837 | 4085.3025 | ITH5 | C
IT | ITH53 |  | IT08000000000219 | BORETTO | 44.8945 | 10.5764 | 7500 | 4996 | NO | 31.225 | 0 | 0 | 0 | 181.105 | 1086.63 | ITH5 | C
IT | ITH53 |  | IT08000000000221 | CADELBOSCO_VILLA_SETA_NUOVO | 44.8109 | 10.6502 | 5000 | 3365 | NO | 21.0312 | 0 | 0 | 0 | 121.9812 | 731.8875 | ITH5 | C
IT | ITH53 |  | IT08000000000230 | LUZZARA | 44.9577 | 10.6993 | 5000 | 4665 | NO | 29.1562 | 0 | 0 | 0 | 169.1062 | 1014.6375 | ITH5 | B
IT | ITH53 |  | IT08000000000235 | RIO_SALICETO | 44.8173 | 10.8091 | 6000 | 6281 | NO | 39.2563 | 0 | 0 | 0 | 227.6863 | 1366.1175 | ITH5 | B
IT | ITH53 |  | IT08000000000238 | SCANDIANO_BOSCO | 44.6353 | 10.6715 | 6000 | 3023 | NO | 18.8938 | 0 | 0 | 0 | 109.5838 | 657.5025 | ITH5 | C
IT | ITH53 |  | IT08000000000222 | CADELBOSCO | 44.7784 | 10.5872 | 8000 | 6445 | NO | 40.2812 | 0 | 0 | 0 | 233.6312 | 1401.7875 | ITH5 | C
IT | ITH53 |  | IT08000000000227 | GATTATICO_PRATICELLO | 44.813 | 10.4701 | 7000 | 5055 | NO | 31.5938 | 0 | 0 | 0 | 183.2438 | 1099.4625 | ITH5 | B
IT | ITH53 |  | IT08000000000228 | GUASTALLA_NORD | 44.9203 | 10.6746 | 12000 | 6865 | NO | 42.9062 | 0 | 0 | 0 | 248.8562 | 1493.1375 | ITH5 | A
IT | ITH54 |  | IT08000000000101 | FINALE_EMILIA_MASSA_FINALESE | 44.8558 | 11.2399 | 5000 | 5156 | NO | 32.225 | 0 | 0 | 0 | 186.905 | 1121.43 | ITH5 | C
IT | ITH54 |  | IT08000000000130 | SAN_PROSPERO | 44.7922 | 11.0316 | 5500 | 6328 | NO | 39.55 | 0 | 0 | 0 | 229.39 | 1376.34 | ITH5 | B
IT | ITH54 |  | IT08000000000111 | MEDOLLA | 44.8494 | 11.0775 | 6000 | 5646 | NO | 35.2875 | 0 | 0 | 0 | 204.6675 | 1228.005 | ITH5 | B
IT | ITH56 |  | IT08000000000064 | CODIGORO | 44.8361 | 12.1215 | 44000 | 10176 | NO | 63.6 | 0 | 0 | 0 | 368.88 | 2213.28 | ITH5 | A
IT | ITH56 |  | IT08000000000065 | COMACCHIO_VALLE_MOLINO | 44.6784 | 12.2068 | 180000 | 175040 | NO | 1094 | 0 | 0 | 0 | 6345.2 | 38071.2 | ITH5 | A
IT | ITH56 |  | IT08000000000070 | FERRARA | 44.8653 | 11.6287 | 240000 | 123379 | YES | 771.1188 | 2467.58 | 1850.685 | 3701.37 | 4472.4888 | 26834.9325 | ITH5 | C
IT | ITH57 |  | IT08000000000203 | BAGNACAVALLO_VILLANOVA | 44.4704 | 12.0483 | 5000 | 4461 | NO | 27.8812 | 0 | 0 | 0 | 161.7112 | 970.2675 | ITH5 | C
IT | ITH57 |  | IT08000000000211 | LUGO_VOLTANA | 44.5466 | 11.93 | 7400 | 3910 | NO | 24.4375 | 0 | 0 | 0 | 141.7375 | 850.425 | ITH5 | B
IT | ITH57 |  | IT08000000000217 | RIOLO_TERME | 44.2712 | 11.731 | 5000 | 5231 | NO | 32.6938 | 0 | 0 | 0 | 189.6237 | 1137.7425 | ITH5 | B
IT | ITH57 |  | IT08000000000208 | CONSELICE | 44.5182 | 11.8437 | 8000 | 6276 | NO | 39.225 | 0 | 0 | 0 | 227.505 | 1365.03 | ITH5 | B
IT | ITH57 |  | IT08000000000205 | BRISIGHELLA | 44.2234 | 11.786 | 9700 | 3741 | NO | 23.3812 | 0 | 0 | 0 | 135.6112 | 813.6675 | ITH5 | B
IT | ITH57 |  | IT08000000000210 | FUSIGNANO | 44.4837 | 11.9711 | 12000 | 11423 | NO | 71.3937 | 0 | 0 | 0 | 414.0837 | 2484.5025 | ITH5 | C
IT | ITH57 |  | IT08000000000204 | BAGNACAVALLO | 44.4234 | 11.9894 | 25000 | 16923 | NO | 105.7688 | 0 | 0 | 0 | 613.4588 | 3680.7525 | ITH5 | C
IT | ITH57 |  | IT08000000000214 | LIDO_DI_CLASSE | 44.3246 | 12.3253 | 30000 | 25943 | NO | 162.1438 | 0 | 0 | 0 | 940.4337 | 5642.6025 | ITH5 | B
IT | ITH57 |  | IT08000000000215 | MARINA_DI_RAVENNA | 44.4658 | 12.2791 | 40000 | 34502 | NO | 215.6375 | 0 | 0 | 0 | 1250.6975 | 7504.185 | ITH5 | C
IT |  |  | IT210000000047 | MAGRÈ_ | 46.2912 | 11.2225 | 9000 | 7006 | NOT KNOWN | 43.7875 | 0 | 0 | 0 | 253.9675 | 1523.805 | ITH1 | B
IT |  |  | IT210000000052 | SAN CANDIDO-SESTO | 46.7066 | 12.3528 | 36000 | 37504 | NOT KNOWN | 234.4 | 0 | 0 | 0 | 1359.52 | 8157.12 | ITH1 | B
IT | ITH41 |  | IT06000000000022 | AVIANO_CASTELLO | 46.0403 | 12.568 | 24000 | 9227 | NO | 57.6687 | 0 | 0 | 0 | 334.4787 | 2006.8725 | ITH4 | C
IT | ITH41 |  | IT06000000000036 | AZZANO_X_VIA_TRIESTE | 45.8762 | 12.7171 | 9200 | 6190 | NO | 38.6875 | 0 | 0 | 0 | 224.3875 | 1346.325 | ITH4 | B
IT | ITH57 |  | IT08000000000218 | RUSSI | 44.3811 | 12.0569 | 50000 | 16551 | NO | 103.4438 | 0 | 0 | 0 | 599.9737 | 3599.8425 | ITH5 | C
IT | ITH57 |  | IT08000000000213 | MASSA_LOMBARDA | 44.4606 | 11.8104 | 80000 | 36969 | NO | 231.0563 | 0 | 0 | 0 | 1340.1262 | 8040.7575 | ITH5 | C
IT | ITH57 |  | IT08000000000202 | ALFONSINE | 44.5171 | 12.036 | 96000 | 12509 | NO | 78.1813 | 0 | 0 | 0 | 453.4513 | 2720.7075 | ITH5 | B
IT | ITH57 |  | IT08000000000209 | FAENZA | 44.2902 | 11.9008 | 100000 | 71840 | NO | 449 | 0 | 0 | 0 | 2604.2 | 15625.2 | ITH5 | B
IT | ITH57 |  | IT08000000000206 | CERVIA | 44.2886 | 12.3148 | 200000 | 153645 | YES | 960.2812 | 3072.9 | 2304.675 | 4609.35 | 5569.6313 | 33417.7875 | ITH5 | C
IT | ITH57 |  | IT08000000000216 | RAVENNA | 44.4454 | 12.2052 | 240000 | 168957 | YES | 1055.9813 | 3379.14 | 2534.355 | 5068.71 | 6124.6912 | 36748.1475 | ITH5 | A
IT | ITH57 |  | IT08000000000212 | LUGO | 44.4368 | 11.9123 | 102874 | 101014 | YES | 631.3375 | 2020.28 | 1515.21 | 3030.42 | 3661.7575 | 21970.545 | ITH5 | B
IT | ITH58 |  | IT08000000000055 | SANTA_SOFIA_CAVATICCIO | 43.9552 | 11.9168 | 5100 | 3243 | NO | 20.2688 | 0 | 0 | 0 | 117.5588 | 705.3525 | ITH5 | A
IT | ITH58 |  | IT08000000000046 | CESENA_PIEVESESTINA | 44.2002 | 12.2107 | 5200 | 2963 | NO | 18.5188 | 0 | 0 | 0 | 107.4087 | 644.4525 | ITH5 | A
IT | ITH58 |  | IT08Q13000000008 | BAGNO_DI_ROMAGNA | 43.8797 | 11.9976 | 7800 | 6502 | NO | 40.6375 | 0 | 0 | 0 | 235.6975 | 1414.185 | ITH5 | C
IT | ITH58 |  | IT08000000000054 | MODIGLIANA_TOSSINO | 44.1669 | 11.8052 | 15240 | 12613 | NO | 78.8312 | 0 | 0 | 0 | 457.2212 | 2743.3275 | ITH5 | B
IT | ITH58 |  | IT08Q13000000001 | MERCATO_SARACENO_BACCIOLINO | 44.0325 | 12.1902 | 15000 | 7943 | NO | 49.6438 | 0 | 0 | 0 | 287.9338 | 1727.6025 | ITH5 | C
IT | ITH58 |  | IT08000000000049 | CESENATICO | 44.1913 | 12.3932 | 120000 | 118856 | NO | 742.85 | 0 | 0 | 0 | 4308.53 | 25851.18 | ITH5 | B
IT | ITH58 |  | IT08000000000056 | SAVIGNANO_SUL_RUBICONE_BASTIA | 44.1107 | 12.403 | 139000 | 98246 | NO | 614.0375 | 0 | 0 | 0 | 3561.4175 | 21368.505 | ITH5 | B
IT | ITH58 |  | IT08000000000048 | CESENA | 44.1696 | 12.273 | 197500 | 97417 | NO | 608.8563 | 0 | 0 | 0 | 3531.3663 | 21188.1975 | ITH5 | A
IT | ITH55 |  | IT08000000000038 | SASSO_MARCONI_BORGONUOVO | 44.4462 | 11.2766 | 7000 | 4264 | NO | 26.65 | 0 | 0 | 0 | 154.57 | 927.42 | ITH5 | A
IT | ITH55 |  | IT08000000000022 | LIZZANO_IN_BELVEDERE_CAPOLUOGO_PANIGALE | 44.1686 | 10.9069 | 8000 | 2866 | NO | 17.9125 | 0 | 0 | 0 | 103.8925 | 623.355 | ITH5 | C
IT | ITH55 |  | IT08000000000032 | SALA_BOLOGNESE_PADULLE | 44.6217 | 11.2653 | 8000 | 7114 | NO | 44.4625 | 0 | 0 | 0 | 257.8825 | 1547.295 | ITH5 | C
IT | ITH55 |  | IT08000000000037 | SANT_AGATA_BOLOGNESE | 44.6651 | 11.1425 | 8000 | 6444 | NO | 40.275 | 0 | 0 | 0 | 233.595 | 1401.57 | ITH5 | B
IT | ITH55 |  | IT08000000000042 | VERGATO | 44.2888 | 11.1131 | 9000 | 6314 | NO | 39.4625 | 0 | 0 | 0 | 228.8825 | 1373.295 | ITH5 | A
IT | ITH55 |  | IT08000000000034 | SAN_GIOVANNI_IN_PERSICETO_DECIMA | 44.7155 | 11.2204 | 9200 | 5485 | NO | 34.2812 | 0 | 0 | 0 | 198.8313 | 1192.9875 | ITH5 | B
IT | ITH55 |  | IT08000000000019 | GRANAROLO_DELL_EMILIA | 44.5602 | 11.4439 | 9500 | 6448 | NO | 40.3 | 0 | 0 | 0 | 233.74 | 1402.44 | ITH5 | B
IT | ITH55 |  | IT08000000000002 | ARGELATO_FUNO | 44.602 | 11.3595 | 9600 | 6310 | NO | 39.4375 | 0 | 0 | 0 | 228.7375 | 1372.425 | ITH5 | B
IT | ITH55 |  | IT08000000000036 | SAN_PIETRO_IN_CASALE | 44.6922 | 11.4068 | 9600 | 9625 | NO | 60.1562 | 0 | 0 | 0 | 348.9062 | 2093.4375 | ITH5 | B
IT | ITH55 |  | IT08000000000033 | SAN_GIORGIO_DI_PIANO | 44.6439 | 11.3875 | 9950 | 6362 | NO | 39.7625 | 0 | 0 | 0 | 230.6225 | 1383.735 | ITH5 | B
IT | ITH55 |  | IT08000000000044 | CASTENASO_NUOVO | 44.5102 | 11.4775 | 11000 | 10147 | NO | 63.4187 | 0 | 0 | 0 | 367.8287 | 2206.9725 | ITH5 | B
IT | ITH58 |  | IT08000000000051 | FORLI | 44.2306 | 12.0878 | 250000 | 158405 | NO | 990.0312 | 0 | 0 | 0 | 5742.1812 | 34453.0875 | ITH5 | A
IT | ITH59 |  | IT08Q11000000001 | NOVAFELTRIA | 43.9014 | 12.2929 | 7000 | 5777 | NO | 36.1063 | 0 | 0 | 0 | 209.4163 | 1256.4975 | ITH5 | B
IT | ITH59 |  | IT08000000000242 | MISANO_ADRIATICO | 43.9662 | 12.7128 | 50000 | 27266 | NO | 170.4125 | 0 | 0 | 0 | 988.3925 | 5930.355 | ITH5 | B
IT | ITH59 |  | IT08000000000240 | CATTOLICA | 43.9586 | 12.728 | 120000 | 108366 | YES | 677.2875 | 2167.32 | 1625.49 | 3250.98 | 3928.2675 | 23569.605 | ITH5 | A
IT | ITH42 |  | IT06000000000018 | TOLMEZZO_CONSORTILE_VIA_DEL_PIOPPETO | 46.3901 | 13.0238 | 143000 | 100341 | YES | 627.1313 | 2006.82 | 1505.115 | 3010.23 | 3637.3612 | 21824.1675 | ITH4 | A
IT | ITH42 |  | IT06000000000019 | TRICESIMO_MORENA | 46.1382 | 13.22 | 7000 | 4218 | NO | 26.3625 | 0 | 0 | 0 | 152.9025 | 917.415 | ITH4 | B
IT | ITH42 |  | IT06000000000058 | PALMANOVA_BORGO_PIAVE | 45.9004 | 13.3287 | 8000 | 4267 | NO | 26.6688 | 0 | 0 | 0 | 154.6788 | 928.0725 | ITH4 | B
IT | ITH41 |  | IT06000000000069 | CORDENONS_VIA_CHIAVORNICCO_PIP | 45.9562 | 12.7065 | 5000 | 206 | NO | 1.2875 | 0 | 0 | 0 | 7.4675 | 44.805 | ITH4 | B
IT | ITH41 |  | IT06000000000002 | FIUME_VENETO_VIA_TAVELLA | 45.9236 | 12.7177 | 8700 | 4005 | NO | 25.0312 | 0 | 0 | 0 | 145.1813 | 871.0875 | ITH4 | B
IT | ITH43 |  | IT06000000000053 | DEPURATORE_DI_GRADISCA_D_ISONZO | 45.8763 | 13.4657 | 11000 | 10562 | NO | 66.0125 | 0 | 0 | 0 | 382.8725 | 2297.235 | ITH4 | B
IT | ITH43 |  | IT06000000000052 | ROMANS_D_ISONZO | 45.8825 | 13.4266 | 6900 | 4358 | NO | 27.2375 | 0 | 0 | 0 | 157.9775 | 947.865 | ITH4 | B
IT | ITH42 |  | IT06000000000098 | SAN_GIORGIO_DI_NOGARO | 45.7602 | 13.232 | 698000 | 100341 | YES | 627.1313 | 2006.82 | 1505.115 | 3010.23 | 3637.3612 | 21824.1675 | ITH4 | A
IT | ITH41 |  | IT06000000000005 | SACILE_LOC_S_ODORICO | 45.9436 | 12.5049 | 11000 | 6030 | NO | 37.6875 | 0 | 0 | 0 | 218.5875 | 1311.525 | ITH4 | B
IT | ITH41 |  | IT06000000000070 | SPILIMBERGO_TAGLIAMENTO_NUOVO | 46.1084 | 12.9071 | 8000 | 2664 | NO | 16.65 | 0 | 0 | 0 | 96.57 | 579.42 | ITH4 | B
IT | ITH44 |  | IT06000000000072 | TRIESTE_ZAULE | 45.6116 | 13.8048 | 67000 | 65745 | NO | 410.9062 | 0 | 0 | 0 | 2383.2562 | 14299.5375 | ITH4 | B
IT | ITH42 |  | IT06000000000030 | MANZANO_CAPOLUOGO | 45.9779 | 13.3882 | 6000 | 1222 | NO | 7.6375 | 0 | 0 | 0 | 44.2975 | 265.785 | ITH4 | B
IT | ITH42 |  | IT06000000000031 | MARTIGNACCO | 46.0873 | 13.143 | 7000 | 4042 | NO | 25.2625 | 0 | 0 | 0 | 146.5225 | 879.135 | ITH4 | A
IT | ITH42 |  | IT06000000000095 | PAGNACCO_PLAINO | 46.0962 | 13.1899 | 5000 | 3212 | NO | 20.075 | 0 | 0 | 0 | 116.435 | 698.61 | ITH4 | B
IT | ITH41 |  | IT06000000000049 | MANIAGO_LOC_PESCHIERA | 46.1676 | 12.7242 | 11600 | 7820 | NO | 48.875 | 0 | 0 | 0 | 283.475 | 1700.85 | ITH4 | B
IT | ITH42 |  | IT06000000000020 | UDINE_VIA_GONARS | 46.0252 | 13.2366 | 200000 | 132742 | YES | 829.6375 | 2654.84 | 1991.13 | 3982.26 | 4811.8975 | 28871.385 | ITH4 | A
IT | ITH42 |  | IT06000000000101 | SAN_VITO_DI_FAGAGNA_SILVELLA | 46.0713 | 13.0595 | 7500 | 6011 | NO | 37.5688 | 0 | 0 | 0 | 217.8987 | 1307.3925 | ITH4 | C
IT | ITH42 |  | IT06000000000097 | SAN_DANIELE_VILLANOVA_NORD | 46.1373 | 12.9563 | 20000 | 5564 | NO | 34.775 | 0 | 0 | 0 | 201.695 | 1210.17 | ITH4 | C
IT | ITH42 |  | IT06000000000093 | BUJA_AVILLA | 46.2043 | 13.0977 | 5000 | 3565 | NO | 22.2812 | 0 | 0 | 0 | 129.2312 | 775.3875 | ITH4 | B
IT | ITH43 |  | IT06000000000041 | CORMONS | 45.9439 | 13.4477 | 12000 | 6296 | NO | 39.35 | 0 | 0 | 0 | 228.23 | 1369.38 | ITH4 | C
IT | ITH43 |  | IT06000000000042 | GORIZIA | 45.9138 | 13.5857 | 54200 | 46606 | NO | 291.2875 | 0 | 0 | 0 | 1689.4675 | 10136.805 | ITH4 | A
IT | ITH43 |  | IT06000000000054 | GRADO | 45.7038 | 13.4579 | 80000 | 18649 | NO | 116.5562 | 0 | 0 | 0 | 676.0262 | 4056.1575 | ITH4 | C
IT | ITH43 |  | IT06000000000063 | DEPURATORE_DI_STARANZANO | 45.7849 | 13.5001 | 62500 | 49046 | NO | 306.5375 | 0 | 0 | 0 | 1777.9175 | 10667.505 | ITH4 | C
IT | ITH42 |  | IT06000000000094 | BUTTRIO | 45.9926 | 13.3338 | 5000 | 2929 | NO | 18.3063 | 0 | 0 | 0 | 106.1763 | 637.0575 | ITH4 | C
IT | ITH42 |  | IT06000000000055 | CASTIONS_DI_STRADA_VIA_LATISANA | 45.8995 | 13.1797 | 5000 | 2602 | NO | 16.2625 | 0 | 0 | 0 | 94.3225 | 565.935 | ITH4 | B
IT | ITH42 |  | IT06000000000056 | CIVIDALE_VIA_ABETI | 46.0842 | 13.4214 | 5000 | 3450 | NO | 21.5625 | 0 | 0 | 0 | 125.0625 | 750.375 | ITH4 | B
IT | ITH42 |  | IT06000000000082 | POZZUOLO_TERENZANO | 46.0016 | 13.204 | 8000 | 6798 | NO | 42.4875 | 0 | 0 | 0 | 246.4275 | 1478.565 | ITH4 | B
IT | ITH42 |  | IT06000000000084 | REANA_DEL_ROIALE | 46.1326 | 13.2583 | 6000 | 4541 | NO | 28.3812 | 0 | 0 | 0 | 164.6112 | 987.6675 | ITH4 | C
IT | ITH42 |  | IT06000000000057 | CIVIDALE_GRUPIGNANO | 46.0802 | 13.4133 | 9000 | 4867 | NO | 30.4188 | 0 | 0 | 0 | 176.4288 | 1058.5725 | ITH4 | B
IT | ITH42 |  | IT06000000000027 | CODROIPO_BELVEDERE | 45.9485 | 12.9896 | 18200 | 16855 | NO | 105.3438 | 0 | 0 | 0 | 610.9937 | 3665.9625 | ITH4 | B
IT | ITH41 |  | IT06000000000013 | CANEVA_LOC_FIASCHETTI | 45.9799 | 12.4804 | 6300 | 1783 | NO | 11.1437 | 0 | 0 | 0 | 64.6337 | 387.8025 | ITH4 | A
IT | ITH41 |  | IT06000000000006 | CORDENONS_VIA_AQUILEIA | 45.9692 | 12.686 | 6000 | 3690 | NO | 23.0625 | 0 | 0 | 0 | 133.7625 | 802.575 | ITH4 | A
IT | ITH42 |  | IT06Q17000000001 | PRADAMANO_LOVARIA | 46.0123 | 13.3095 | 6000 | 5967 | NO | 37.2938 | 0 | 0 | 0 | 216.3038 | 1297.8225 | ITH4 | B
IT | ITH42 |  | IT06Q190000001 | SAPPADA_LERPA | 46.563 | 12.668 | 6000 | 3123 | NOT KNOWN | 19.5188 | 0 | 0 | 0 | 113.2087 | 679.2525 | ITH3 | B
IT | ITH41 |  | IT06000000000079 | PORDENONE_VIA_BURIDA | 45.9491 | 12.6449 | 50000 | 37096 | NO | 231.85 | 0 | 0 | 0 | 1344.73 | 8068.38 | ITH4 | A
IT | ITH41 |  | IT06000000000078 | PORDENONE_VIA_SAVIO_VALLENONCELLO | 45.9223 | 12.6498 | 15000 | 2800 | NO | 17.5 | 0 | 0 | 0 | 101.5 | 609 | ITH4 | B
IT | ITH42 |  | IT06000000000090 | OSOPPO_CAPOLUOGO | 46.2501 | 13.0746 | 5000 | 2386 | NO | 14.9125 | 0 | 0 | 0 | 86.4925 | 518.955 | ITH4 | B
IT | ITH42 |  | IT06000000000029 | LATISANA_VIA_LIGNANO_NORD | 45.771 | 13.0323 | 14000 | 8139 | NO | 50.8688 | 0 | 0 | 0 | 295.0387 | 1770.2325 | ITH4 | B
IT | ITH44 |  | IT06000000000008 | TRIESTE_SERVOLA | 45.6253 | 13.7789 | 190000 | 158031 | YES | 987.6938 | 3160.62 | 2370.465 | 4740.93 | 5728.6237 | 34371.7425 | ITH4 | A
IT | ITH41 |  | IT06000000000003 | FONTANAFREDDA_VIA_S_EGIDIO | 45.9636 | 12.5622 | 7500 | 7220 | NO | 45.125 | 0 | 0 | 0 | 261.725 | 1570.35 | ITH4 | B
IT | ITH41 |  | IT06000000000004 | SAN_VITO_AL_TAGLIAMENTO_VIA_ZUCCHERIFICIO | 45.9059 | 12.8503 | 28000 | 26800 | NO | 167.5 | 0 | 0 | 0 | 971.5 | 5829 | ITH4 | A
IT | ITH41 |  | IT06000000000077 | PORCIA_VIA_DEL_PLATANO | 45.9516 | 12.6135 | 10000 | 8780 | NO | 54.875 | 0 | 0 | 0 | 318.275 | 1909.65 | ITH4 | A
IT | ITH42 |  | IT06000000000085 | REMANZACCO_CASALI_BATTIFERRO | 46.068 | 13.3303 | 6000 | 4277 | NO | 26.7313 | 0 | 0 | 0 | 155.0412 | 930.2475 | ITH4 | A
IT | ITH42 |  | IT06000000000076 | GEMONA_VIA_CHIANEIT | 46.2534 | 13.1248 | 13000 | 9719 | NO | 60.7438 | 0 | 0 | 0 | 352.3138 | 2113.8825 | ITH4 | B
IT | ITH42 |  | IT06000000000081 | GONARS_VIA_MOLINI | 45.8929 | 13.2276 | 6700 | 4553 | NO | 28.4563 | 0 | 0 | 0 | 165.0463 | 990.2775 | ITH4 | B
IT | ITH42 |  | IT06000000000044 | LIGNANO_SABBIADORO | 45.6837 | 13.1073 | 86400 | 82537 | YES | 515.8563 | 1650.74 | 1238.055 | 2476.11 | 2991.9662 | 17951.7975 | ITH4 | A
IT | ITH41 |  | IT06000000000007 | CORDENONS_VIA_CHIAVORNICCO | 45.9569 | 12.7044 | 8000 | 7654 | NO | 47.8375 | 0 | 0 | 0 | 277.4575 | 1664.745 | ITH4 | B
IT | ITC41 |  | IT03160128000382 | DP01208702_LAVENO_MOMBELLO | 45.902 | 8.6338 | 30000 | 17035 | NO | 106.4688 | 0 | 0 | 0 | 617.5187 | 3705.1125 | ITC4 | B
IT | ITC41 |  | IT03160128000370 | DP01203702_CASALZUIGNO | 45.8975 | 8.7073 | 13100 | 10320 | NO | 64.5 | 0 | 0 | 0 | 374.1 | 2244.6 | ITC4 | B
IT | ITC41 |  | IT03160128000372 | DP01205801_CUASSO_AL_MONTE | 45.8981 | 8.8886 | 22000 | 15430 | NO | 96.4375 | 0 | 0 | 0 | 559.3375 | 3356.025 | ITC4 | B
IT | ITC41 |  | IT03160128000373 | DP01206401_DAVERIO | 45.7664 | 8.761 | 5000 | 4084 | NO | 25.525 | 0 | 0 | 0 | 148.045 | 888.27 | ITC4 | A
IT | ITC41 |  | IT03160128000374 | DP01206901_FERRERA_DI_VARESE | 45.9365 | 8.7795 | 16000 | 16000 | NO | 100 | 0 | 0 | 0 | 580 | 3480 | ITC4 | B
IT | ITC41 |  | IT03160128000375 | DP01207201_GAVIRATE_VARESE_LAGO | 45.8392 | 8.7013 | 110000 | 96233 | YES | 601.4563 | 1924.66 | 1443.495 | 2886.99 | 3488.4462 | 20930.6775 | ITC4 | A
IT | ITC41 |  | IT03160128000379 | DP01208001_GORNATE_OLONA | 45.7242 | 8.8691 | 82500 | 44473 | YES | 277.9563 | 889.46 | 667.095 | 1334.19 | 1612.1462 | 9672.8775 | ITC4 | A
IT | ITC41 |  | IT03160128000381 | DP01208601_LAVENA_PONTE_TRESA | 45.9723 | 8.8497 | 9000 | 8629 | NO | 53.9313 | 0 | 0 | 0 | 312.8013 | 1876.8075 | ITC4 | A
IT | ITC41 |  | IT03160128000384 | DP01209001_LONATE_POZZOLO | 45.5764 | 8.7613 | 450000 | 365665 | YES | 2285.4062 | 7313.3 | 5484.975 | 10969.95 | 13255.3563 | 79532.1375 | ITC4 | B
IT | ITC41 |  | IT03160128000385 | DP01209201_LUINO_VOLDOMINO | 45.9893 | 8.7444 | 25000 | 22402 | NO | 140.0125 | 0 | 0 | 0 | 812.0725 | 4872.435 | ITC4 | B
IT | ITC41 |  | IT03160128000386 | DP01209403_MACCAGNO | 46.0439 | 8.7457 | 7000 | 3287 | NO | 20.5437 | 0 | 0 | 0 | 119.1537 | 714.9225 | ITC4 | B
IT | ITC41 |  | IT03160128000388 | DP01210401_MONVALLE | 45.8492 | 8.6246 | 12500 | 12271 | NO | 76.6938 | 0 | 0 | 0 | 444.8238 | 2668.9425 | ITC4 | A
IT | ITC41 |  | IT03160128000389 | DP01210601_MORNAGO | 45.7243 | 8.7284 | 7000 | 6402 | NO | 40.0125 | 0 | 0 | 0 | 232.0725 | 1392.435 | ITC4 | B
IT | ITC41 |  | IT03160128000391 | DP01210801_OLGIATE_OLONA | 45.6253 | 8.8951 | 200000 | 91774 | YES | 573.5875 | 1835.48 | 1376.61 | 2753.22 | 3326.8075 | 19960.845 | ITC4 | B
IT | ITC41 |  | IT03160128000392 | DP01210901_ORIGGIO | 45.5805 | 9.0026 | 75000 | 51602 | YES | 322.5125 | 1032.04 | 774.03 | 1548.06 | 1870.5725 | 11223.435 | ITC4 | B
IT | ITC41 |  | IT03160128000393 | DP01211401_PORTO_VAL_TRAVAGLIA_CAVE_DEL_TRIGO | 45.9716 | 8.7015 | 12000 | 3899 | NO | 24.3688 | 0 | 0 | 0 | 141.3388 | 848.0325 | ITC4 | A
IT | ITC41 |  | IT03160128000394 | DP01212001_SESTO_CALENDE | 45.7141 | 8.6597 | 12000 | 11765 | NO | 73.5312 | 0 | 0 | 0 | 426.4812 | 2558.8875 | ITC4 | B
IT | ITC41 |  | IT03160128000396 | DP01212301_SOMMA_LOMBARDO_CA_BAGAGGIO | 45.6742 | 8.6904 | 20000 | 18323 | NO | 114.5188 | 0 | 0 | 0 | 664.2088 | 3985.2525 | ITC4 | B
IT | ITC41 |  | IT03160128000398 | DP01213301_VARESE_OLONA | 45.8115 | 8.8585 | 120000 | 74332 | YES | 464.575 | 1486.64 | 1114.98 | 2229.96 | 2694.535 | 16167.21 | ITC4 | A
IT | ITC41 |  | IT03160128000399 | DP01213802_VERGIATE_S_EUROSIA | 45.7173 | 8.7083 | 10000 | 8954 | NO | 55.9625 | 0 | 0 | 0 | 324.5825 | 1947.495 | ITC4 | A
IT | ITC41 |  | IT03160128000400 | DP01213901_VIGGIU | 45.8602 | 8.915 | 6000 | 5989 | NO | 37.4312 | 0 | 0 | 0 | 217.1012 | 1302.6075 | ITC4 | B
IT | ITC42 |  | IT03160128000402 | DP01301901_BELLAGIO | 45.9777 | 9.2546 | 9000 | 6017 | NO | 37.6063 | 0 | 0 | 0 | 218.1162 | 1308.6975 | ITC4 | A
IT | ITC42 |  | IT03160128000403 | DP01303401_BULGAROGRASSO | 45.7423 | 9.0152 | 96520 | 88000 | NO | 550 | 0 | 0 | 0 | 3190 | 19140 | ITC4 | B
IT | ITC42 |  | IT03160128000404 | DP01303801_CAGNO | 45.8116 | 8.9248 | 8000 | 7500 | NO | 46.875 | 0 | 0 | 0 | 271.875 | 1631.25 | ITC4 | B
IT | ITC42 |  | IT03160128000406 | DP01304601_CARIMATE | 45.6894 | 9.1222 | 98000 | 73283 | YES | 458.0188 | 1465.66 | 1099.245 | 2198.49 | 2656.5087 | 15939.0525 | ITC4 | B
IT | ITC42 |  | IT03160128000407 | DP01304701_CARLAZZO | 46.0418 | 9.159 | 10000 | 4563 | NO | 28.5188 | 0 | 0 | 0 | 165.4087 | 992.4525 | ITC4 | A
IT | ITC42 |  | IT03Q11000000049 | DP01307401_COLONNO | 45.9533 | 9.1436 | 30000 | 8626 | NO | 53.9125 | 0 | 0 | 0 | 312.6925 | 1876.155 | ITC4 | C
IT | ITC42 |  | IT03160128000408 | DP01307501_COMO | 45.8061 | 9.0783 | 208167 | 166779 | NO | 1042.3688 | 0 | 0 | 0 | 6045.7388 | 36274.4325 | ITC4 | A
IT | ITC42 |  | IT03160128000409 | DP01308301_CREMIA | 46.0782 | 9.2773 | 8000 | 4077 | NO | 25.4813 | 0 | 0 | 0 | 147.7912 | 886.7475 | ITC4 | B
IT | ITC42 |  | IT03160128000410 | DP01310201_FINO_MORNASCO_ALTO_SEVESO | 45.7505 | 9.0615 | 140000 | 75300 | NO | 470.625 | 0 | 0 | 0 | 2729.625 | 16377.75 | ITC4 | B
IT | ITC42 |  | IT03160128000411 | DP01310202_FINO_MORNASCO_LIVESCIA | 45.7389 | 9.0386 | 43300 | 24000 | NO | 150 | 0 | 0 | 0 | 870 | 5220 | ITC4 | B
IT | ITC42 |  | IT03160128000412 | DP01311201_GRAVEDONA | 46.1403 | 9.3021 | 26000 | 13980 | NO | 87.375 | 0 | 0 | 0 | 506.775 | 3040.65 | ITC4 | A
IT | ITC42 |  | IT03Q11000000050 | DP01312201_LANZO_D_INTELVI | 45.9848 | 9.0467 | 10000 | 4647 | NO | 29.0438 | 0 | 0 | 0 | 168.4538 | 1010.7225 | ITC4 | B
IT | ITC42 |  | IT03160128000414 | DP01312801_LIMIDO_COMASCO | 45.6843 | 8.9697 | 28800 | 21980 | NO | 137.375 | 0 | 0 | 0 | 796.775 | 4780.65 | ITC4 | B
IT | ITC42 |  | IT03160128000415 | DP01314301_MARIANO_COMENSE | 45.687 | 9.1658 | 60000 | 59950 | NO | 374.6875 | 0 | 0 | 0 | 2173.1875 | 13039.125 | ITC4 | B
IT | ITC42 |  | IT03160128000416 | DP01314501_MENAGGIO | 46.0399 | 9.2452 | 20000 | 13195 | NO | 82.4688 | 0 | 0 | 0 | 478.3187 | 2869.9125 | ITC4 | C
IT | ITC42 |  | IT03160128000417 | DP01314701_MERONE | 45.7681 | 9.2431 | 125000 | 117465 | YES | 734.1562 | 2349.3 | 1761.975 | 3523.95 | 4258.1062 | 25548.6375 | ITC4 | B
IT | ITC42 |  | IT03160128000419 | DP01318901_PORLEZZA | 46.0332 | 9.1347 | 9750 | 6306 | NO | 39.4125 | 0 | 0 | 0 | 228.5925 | 1371.555 | ITC4 | A
IT | ITC42 |  | IT03160128000420 | DP01319901_RONAGO | 45.8271 | 8.9928 | 22500 | 16500 | NO | 103.125 | 0 | 0 | 0 | 598.125 | 3588.75 | ITC4 | B
IT | ITC44 |  | IT03160128000421 | DP01400401_APRICA | 46.1489 | 10.1275 | 9000 | 12578 | NO | 78.6125 | 0 | 0 | 0 | 455.9525 | 2735.715 | ITC4 | C
IT | ITC44 |  | IT03160128000422 | DP01400501_ARDENNO | 46.1593 | 9.6495 | 24000 | 23890 | NO | 149.3125 | 0 | 0 | 0 | 866.0125 | 5196.075 | ITC4 | B
IT | ITC44 |  | IT03160128000424 | DP01402001_CHIURO | 46.1632 | 9.9889 | 10000 | 7000 | NO | 43.75 | 0 | 0 | 0 | 253.75 | 1522.5 | ITC4 | A
IT | ITC44 |  | IT03160128000426 | DP01402702_DUBINO_NUOVA_OLONIO | 46.1692 | 9.4251 | 5000 | 4000 | NO | 25 | 0 | 0 | 0 | 145 | 870 | ITC4 | A
IT | ITC44 |  | IT03160128000427 | DP01403201_GORDONA_AREA_IND_LE | 46.27 | 9.3844 | 25000 | 23595 | NO | 147.4688 | 0 | 0 | 0 | 855.3188 | 5131.9125 | ITC4 | A
IT | ITC44 |  | IT03160128000428 | DP01403702_LIVIGNO | 46.5668 | 10.1527 | 32000 | 25000 | NO | 156.25 | 0 | 0 | 0 | 906.25 | 5437.5 | ITC4 | C
IT | ITC44 |  | IT03160128000429 | DP01403801_LOVERO | 46.2321 | 10.2187 | 21500 | 15000 | NO | 93.75 | 0 | 0 | 0 | 543.75 | 3262.5 | ITC4 | C
IT | ITC44 |  | IT03Q11000000052 | DP01404301_MESE | 46.2999 | 9.3788 | 16500 | 16500 | NO | 103.125 | 0 | 0 | 0 | 598.125 | 3588.75 | ITC4 | B
IT | ITC44 |  | IT03160128000430 | DP01404501_MORBEGNO | 46.1441 | 9.5585 | 18000 | 16909 | NO | 105.6812 | 0 | 0 | 0 | 612.9512 | 3677.7075 | ITC4 | B
IT | ITC44 |  | IT03160128000433 | DP01405601_ROGOLO | 46.1459 | 9.4812 | 30000 | 15072 | NO | 94.2 | 0 | 0 | 0 | 546.36 | 3278.16 | ITC4 | B
IT | ITC44 |  | IT03160128000434 | DP01405702_SAMOLACO | 46.2259 | 9.4217 | 8500 | 7000 | NO | 43.75 | 0 | 0 | 0 | 253.75 | 1522.5 | ITC4 | C
IT | ITC44 |  | IT03160128000435 | DP01406101_SONDRIO | 46.1622 | 9.8544 | 49500 | 49500 | NO | 309.375 | 0 | 0 | 0 | 1794.375 | 10766.25 | ITC4 | A
IT | ITC44 |  | IT03160128000436 | DP01406504_TEGLIO | 46.1597 | 10.0113 | 30000 | 21201 | NO | 132.5062 | 0 | 0 | 0 | 768.5362 | 4611.2175 | ITC4 | B
IT | ITC44 |  | IT03160128000437 | DP01406701_TORRE_S_MARIA | 46.2132 | 9.8661 | 20500 | 17284 | NO | 108.025 | 0 | 0 | 0 | 626.545 | 3759.27 | ITC4 | C
IT | ITC44 |  | IT03160128000438 | DP01407201_VALDISOTTO | 46.4152 | 10.3496 | 40000 | 25140 | NO | 157.125 | 0 | 0 | 0 | 911.325 | 5467.95 | ITC4 | C
IT | ITC44 |  | IT03160128000439 | DP01407401_VAL_MASINO | 46.2065 | 9.6353 | 5000 | 2200 | NO | 13.75 | 0 | 0 | 0 | 79.75 | 478.5 | ITC4 | C
IT | ITC4C |  | IT03160128000440 | DP01500201_ABBIATEGRASSO | 45.3898 | 8.8983 | 37000 | 36216 | NO | 226.35 | 0 | 0 | 0 | 1312.83 | 7876.98 | ITC4 | B
IT | ITC4C |  | IT03160128000441 | DP01501101_ASSAGO | 45.3992 | 9.1393 | 160000 | 120948 | YES | 755.925 | 2418.96 | 1814.22 | 3628.44 | 4384.365 | 26306.19 | ITC4 | A
IT | ITC4C |  | IT03160128000442 | DP01501201_BAREGGIO | 45.4685 | 8.9995 | 64800 | 45180 | NO | 282.375 | 0 | 0 | 0 | 1637.775 | 9826.65 | ITC4 | A
IT | ITC4C |  | IT03160128000443 | DP01501501_BASIGLIO | 45.3535 | 9.1612 | 16300 | 9048 | NO | 56.55 | 0 | 0 | 0 | 327.99 | 1967.94 | ITC4 | A
IT | ITC4C |  | IT03160128000445 | DP01502401_BINASCO | 45.3233 | 9.0916 | 29700 | 17964 | NO | 112.275 | 0 | 0 | 0 | 651.195 | 3907.17 | ITC4 | B
IT | ITC4C |  | IT03160128000446 | DP01503201_BRESSO_SEVESO_SUD | 45.5254 | 9.1963 | 240000 | 209929 | YES | 1312.0563 | 4198.58 | 3148.935 | 6297.87 | 7609.9262 | 45659.5575 | ITC4 | A
IT | ITC4C |  | IT03Q11000000053 | DP01504201_CALVIGNASCO | 45.3252 | 9.027 | 15900 | 10069 | NO | 62.9313 | 0 | 0 | 0 | 365.0013 | 2190.0075 | ITC4 | B
IT | ITC4C |  | IT03160128000447 | DP01504601_CANEGRATE_OLONA_NORD | 45.5732 | 8.9434 | 151800 | 137958 | YES | 862.2375 | 2759.16 | 2069.37 | 4138.74 | 5000.9775 | 30005.865 | ITC4 | A
IT | ITC4C |  | IT03160128000449 | DP01505902_CASSANO_D_ADDA | 45.5102 | 9.5009 | 128800 | 109826 | YES | 686.4125 | 2196.52 | 1647.39 | 3294.78 | 3981.1925 | 23887.155 | ITC4 | A
IT | ITC4C |  | IT03160128000450 | DP01507801_CISLIANO | 45.4446 | 9.0012 | 5000 | 4571 | NO | 28.5687 | 0 | 0 | 0 | 165.6987 | 994.1925 | ITC4 | B
IT | ITC4C |  | IT03160128000451 | DP01510101_DRESANO | 45.3773 | 9.3495 | 7700 | 6623 | NO | 41.3938 | 0 | 0 | 0 | 240.0838 | 1440.5025 | ITC4 | B
IT | ITC4C |  | IT03160128000452 | DP01510301_GAGGIANO | 45.3984 | 9.0371 | 9270 | 8242 | NO | 51.5125 | 0 | 0 | 0 | 298.7725 | 1792.635 | ITC4 | B
IT | ITC4C |  | IT03160128000453 | DP01511501_LACCHIARELLA | 45.3174 | 9.1578 | 25500 | 19395 | NO | 121.2188 | 0 | 0 | 0 | 703.0687 | 4218.4125 | ITC4 | C
IT | ITC41 |  | IT03Q11000000048 | DP01511601_ORIGGIO_EST_LAINATE | 45.5858 | 9.0277 | 31660 | 7912 | NO | 49.45 | 0 | 0 | 0 | 286.81 | 1720.86 | ITC4 | B
IT | ITC4C |  | IT03160128000454 | DP01512501_LOCATE_DI_TRIULZI | 45.3462 | 9.22 | 79300 | 59132 | NO | 369.575 | 0 | 0 | 0 | 2143.535 | 12861.21 | ITC4 | C
IT | ITC4C |  | IT03160128000455 | DP01514001_MELEGNANO | 45.3503 | 9.3372 | 30000 | 25920 | NO | 162 | 0 | 0 | 0 | 939.6 | 5637.6 | ITC4 | B
IT | ITC4C |  | IT03160128000456 | DP01514601_MILANO_NOSEDO | 45.4264 | 9.2217 | 1250000 | 1116928 | NO | 6980.8 | 0 | 0 | 0 | 40488.64 | 242931.84 | ITC4 | A
IT | ITC4C |  | IT03160128000457 | DP01514602_MILANO_S_ROCCO | 45.3932 | 9.1837 | 1050000 | 750863 | NO | 4692.8938 | 0 | 0 | 0 | 27218.7837 | 163312.7025 | ITC4 | B
IT | ITC4C |  | IT03160128000458 | DP01514901_MONZA_S_ROCCO | 45.5598 | 9.2721 | 700000 | 690789 | YES | 4317.4313 | 13815.78 | 10361.835 | 20723.67 | 25041.1012 | 150246.6075 | ITC4 | A
IT | ITC4C |  | IT03160128000459 | DP01515101_MOTTA_VISCONTI | 45.2809 | 8.9888 | 8000 | 7603 | NO | 47.5188 | 0 | 0 | 0 | 275.6087 | 1653.6525 | ITC4 | B
IT | ITC4C |  | IT03160128000460 | DP01515401_PARABIAGO_CERRO_MAGGIORE | 45.5612 | 8.9643 | 32600 | 28023 | NO | 175.1437 | 0 | 0 | 0 | 1015.8337 | 6095.0025 | ITC4 | B
IT | ITC4C |  | IT03160128000465 | DP01518101_RESCALDINA | 45.612 | 8.9675 | 17100 | 17837 | NO | 111.4813 | 0 | 0 | 0 | 646.5913 | 3879.5475 | ITC4 | A
IT | ITC4C |  | IT03160128000466 | DP01518401_ROBECCO_SUL_NAVIGLIO | 45.4153 | 8.8745 | 340000 | 264600 | YES | 1653.75 | 5292 | 3969 | 7938 | 9591.75 | 57550.5 | ITC4 | C
IT | ITC4C |  | IT03160128000467 | DP01518901_ROZZANO | 45.3877 | 9.1656 | 122400 | 56157 | NO | 350.9812 | 0 | 0 | 0 | 2035.6912 | 12214.1475 | ITC4 | B
IT | ITC4C |  | IT03160128000468 | DP01519101_S_COLOMBANO_AL_LAMBRO | 45.185 | 9.5008 | 15400 | 19961 | NO | 124.7563 | 0 | 0 | 0 | 723.5863 | 4341.5175 | ITC4 | B
IT | ITC4C |  | IT03160128000469 | DP01519501_S_GIULIANO_M_SE_OVEST | 45.382 | 9.262 | 30000 | 17078 | NO | 106.7375 | 0 | 0 | 0 | 619.0775 | 3714.465 | ITC4 | A
IT | ITC4C |  | IT03160128000470 | DP01519502_S_GIULIANO_M_SE_EST | 45.3943 | 9.3081 | 120500 | 80198 | YES | 501.2375 | 1603.96 | 1202.97 | 2405.94 | 2907.1775 | 17443.065 | ITC4 | B
IT | ITC4C |  | IT03160128000471 | DP01520901_SESTO_S_GIOVANNI | 45.5217 | 9.258 | 124200 | 97953 | YES | 612.2063 | 1959.06 | 1469.295 | 2938.59 | 3550.7963 | 21304.7775 | ITC4 | A
IT | ITC4C |  | IT03160128000472 | DP01521001_SETTALA | 45.4327 | 9.3945 | 56300 | 54734 | NO | 342.0875 | 0 | 0 | 0 | 1984.1075 | 11904.645 | ITC4 | A
IT | ITC4C |  | IT03160128000473 | DP01522001_TREZZANO_SUL_NAVIGLIO | 45.4129 | 9.0867 | 52000 | 35541 | NO | 222.1313 | 0 | 0 | 0 | 1288.3613 | 7730.1675 | ITC4 | A
IT | ITC4C |  | IT03160128000474 | DP01522401_TRUCCAZZANO | 45.4757 | 9.4321 | 189200 | 188878 | YES | 1180.4875 | 3777.56 | 2833.17 | 5666.34 | 6846.8275 | 41080.965 | ITC4 | A
IT | ITC4C |  | IT03160128000475 | DP01522601_TURBIGO | 45.5199 | 8.7275 | 46600 | 11865 | NO | 74.1562 | 0 | 0 | 0 | 430.1062 | 2580.6375 | ITC4 | B
IT | ITC4D |  | IT03160128000477 | DP01524101_VIMERCATE | 45.5896 | 9.3741 | 104000 | 75985 | YES | 474.9062 | 1519.7 | 1139.775 | 2279.55 | 2754.4563 | 16526.7375 | ITC4 | A
IT | ITC4C |  | IT03160128000478 | DP01524601_ZELO_SURRIGONE | 45.3815 | 8.986 | 8400 | 6139 | NO | 38.3687 | 0 | 0 | 0 | 222.5387 | 1335.2325 | ITC4 | B
IT | ITC46 |  | IT03160128000479 | DP01601001_ANTEGNATE | 45.4782 | 9.7908 | 5000 | 3950 | NO | 24.6875 | 0 | 0 | 0 | 143.1875 | 859.125 | ITC4 | B
IT | ITC46 |  | IT03160128000480 | DP01601801_BAGNATICA | 45.6483 | 9.7796 | 120000 | 90047 | YES | 562.7938 | 1800.94 | 1350.705 | 2701.41 | 3264.2037 | 19585.2225 | ITC4 | B
IT | ITC46 |  | IT03160128000481 | DP01602401_BERGAMO | 45.6722 | 9.6377 | 220000 | 186332 | NO | 1164.575 | 0 | 0 | 0 | 6754.535 | 40527.21 | ITC4 | A
IT | ITC46 |  | IT03160128000482 | DP01602801_BOLGARE | 45.6269 | 9.8139 | 8500 | 6804 | NO | 42.525 | 0 | 0 | 0 | 246.645 | 1479.87 | ITC4 | B
IT | ITC46 |  | IT03160128000483 | DP01602902_BOLTIERE | 45.5954 | 9.5619 | 26000 | 24780 | NO | 154.875 | 0 | 0 | 0 | 898.275 | 5389.65 | ITC4 | B
IT | ITC46 |  | IT03160128000484 | DP01603401_BOTTANUCO | 45.6298 | 9.5109 | 5000 | 4935 | NO | 30.8438 | 0 | 0 | 0 | 178.8937 | 1073.3625 | ITC4 | B
IT | ITC46 |  | IT03160128000486 | DP01603701_BREMBATE | 45.597 | 9.5431 | 185000 | 163944 | YES | 1024.65 | 3278.88 | 2459.16 | 4918.32 | 5942.97 | 35657.82 | ITC4 | B
IT | ITC46 |  | IT03160128000489 | DP01604301_CALCINATE | 45.6123 | 9.7976 | 12000 | 7052 | NO | 44.075 | 0 | 0 | 0 | 255.635 | 1533.81 | ITC4 | B
IT | ITC46 |  | IT03160128000490 | DP01604401_CALCIO | 45.5052 | 9.8585 | 10000 | 5965 | NO | 37.2812 | 0 | 0 | 0 | 216.2312 | 1297.3875 | ITC4 | B
IT | ITC46 |  | IT03160128000492 | DP01606001_CASNIGO | 45.8052 | 9.8694 | 75000 | 21780 | NO | 136.125 | 0 | 0 | 0 | 789.525 | 4737.15 | ITC4 | B
IT | ITC46 |  | IT03160128000498 | DP01607301_CHIUDUNO | 45.6404 | 9.8566 | 6000 | 5746 | NO | 35.9125 | 0 | 0 | 0 | 208.2925 | 1249.755 | ITC4 | B
IT | ITC46 |  | IT03Q13000000124 | DP01607402_CISANO_BERGAMASCO_TORCHIO | 45.7342 | 9.459 | 9114 | 7918 | NO | 49.4875 | 0 | 0 | 0 | 287.0275 | 1722.165 | ITC4 | A
IT | ITC46 |  | IT03160128000500 | DP01607601_CIVIDATE_AL_PIANO | 45.5501 | 9.8351 | 8000 | 6285 | NO | 39.2812 | 0 | 0 | 0 | 227.8312 | 1366.9875 | ITC4 | B
IT | ITC46 |  | IT03160128000501 | DP01607701_CLUSONE | 45.8745 | 9.9173 | 20000 | 12095 | NO | 75.5938 | 0 | 0 | 0 | 438.4438 | 2630.6625 | ITC4 | C
IT | ITC46 |  | IT03160129000503 | DP01607901_COLOGNO_AL_SERIO | 45.5566 | 9.7011 | 107000 | 73351 | YES | 458.4437 | 1467.02 | 1100.265 | 2200.53 | 2658.9737 | 15953.8425 | ITC4 | A
IT | ITC46 |  | IT03160129000505 | DP01608601_COSTA_VOLPINO | 45.816 | 10.0997 | 65000 | 71151 | NO | 444.6937 | 0 | 0 | 0 | 2579.2238 | 15475.3425 | ITC4 | B
IT | ITC46 |  | IT03160129000506 | DP01608701_COVO | 45.4922 | 9.7613 | 23320 | 22207 | NO | 138.7938 | 0 | 0 | 0 | 805.0038 | 4830.0225 | ITC4 | B
IT | ITC4C |  | IT03160128000463 | DP01517001_PERO_OLONA_SUD | 45.4988 | 9.0882 | 620600 | 594809 | YES | 3717.5563 | 11896.18 | 8922.135 | 17844.27 | 21561.8262 | 129370.9575 | ITC4 | A
IT | ITC4C |  | IT03160128000464 | DP01517101_PESCHIERA_BORROMEO | 45.4212 | 9.2946 | 566000 | 419978 | YES | 2624.8625 | 8399.56 | 6299.67 | 12599.34 | 15224.2025 | 91345.215 | ITC4 | A
IT | ITC46 |  | IT03Q170000001 | DP01607805_COLERE | 45.9724 | 10.1072 | 9800 | 5688 | NO | 35.55 | 0 | 0 | 0 | 206.19 | 1237.14 | ITC4 | C
IT | ITC46 |  | IT03160128000143 | DP01624601_ZOGNO | 45.7882 | 9.6436 | 25000 | 21147 | NO | 132.1688 | 0 | 0 | 0 | 766.5788 | 4599.4725 | ITC4 | A
IT | ITC41 |  | IT03160128000360 | DP01200301_ANGERA | 45.7683 | 8.5897 | 20000 | 14269 | NO | 89.1812 | 0 | 0 | 0 | 517.2512 | 3103.5075 | ITC4 | B
IT | ITC41 |  | IT03160128000361 | DP01200401_ARCISATE | 45.8648 | 8.8725 | 22000 | 15623 | NO | 97.6438 | 0 | 0 | 0 | 566.3338 | 3398.0025 | ITC4 | B
IT | ITC41 |  | IT03160128000362 | DP01201302_BESOZZO | 45.8384 | 8.6756 | 9333 | 8148 | NO | 50.925 | 0 | 0 | 0 | 295.365 | 1772.19 | ITC4 | A
IT | ITC41 |  | IT03160128000366 | DP01202901_CAIRATE | 45.6863 | 8.8796 | 45000 | 42954 | NO | 268.4625 | 0 | 0 | 0 | 1557.0825 | 9342.495 | ITC4 | B
IT | ITC41 |  | IT03160128000367 | DP01203001_CANTELLO | 45.8163 | 8.903 | 5000 | 5939 | NO | 37.1187 | 0 | 0 | 0 | 215.2887 | 1291.7325 | ITC4 | B
IT | ITC41 |  | IT03160128000368 | DP01203401_CARONNO_PERTUSELLA | 45.583 | 9.0414 | 400000 | 113411 | YES | 708.8188 | 2268.22 | 1701.165 | 3402.33 | 4111.1488 | 24666.8925 | ITC4 | A
IT | ITC46 |  | IT03160129000509 | DP01610101_FONTANELLA | 45.4638 | 9.7984 | 5000 | 4720 | NO | 29.5 | 0 | 0 | 0 | 171.1 | 1026.6 | ITC4 | B
IT | ITC46 |  | IT03160129000510 | DP01611301_GHISALBA | 45.5861 | 9.7482 | 12000 | 10642 | NO | 66.5125 | 0 | 0 | 0 | 385.7725 | 2314.635 | ITC4 | A
IT | ITC46 |  | IT03160129000511 | DP01611401_GORLAGO | 45.661 | 9.819 | 10000 | 8972 | NO | 56.075 | 0 | 0 | 0 | 325.235 | 1951.41 | ITC4 | B
IT | ITC46 |  | IT03160129000512 | DP01611701_GRASSOBBIO | 45.6485 | 9.7341 | 13000 | 9479 | NO | 59.2438 | 0 | 0 | 0 | 343.6138 | 2061.6825 | ITC4 | B
IT | ITC46 |  | IT03160129000514 | DP01612002_GRUMELLO_DEL_MONTE_CAMPAGNA | 45.629 | 9.8711 | 10000 | 9832 | NO | 61.45 | 0 | 0 | 0 | 356.41 | 2138.46 | ITC4 | B
IT | ITC46 |  | IT03160129000516 | DP01612901_LURANO | 45.5611 | 9.6507 | 91300 | 76530 | YES | 478.3125 | 1530.6 | 1147.95 | 2295.9 | 2774.2125 | 16645.275 | ITC4 | B
IT | ITC46 |  | IT03160129000517 | DP01613301_MARTINENGO | 45.5616 | 9.7693 | 10000 | 9190 | NO | 57.4375 | 0 | 0 | 0 | 333.1375 | 1998.825 | ITC4 | A
IT | ITC46 |  | IT03160129000519 | DP01614201_MOZZANICA | 45.4624 | 9.696 | 145600 | 120000 | YES | 750 | 2400 | 1800 | 3600 | 4350 | 26100 | ITC4 | C
IT | ITC46 |  | IT03160129000520 | DP01614901_ONORE | 45.8905 | 10.0009 | 16440 | 11104 | NO | 69.4 | 0 | 0 | 0 | 402.52 | 2415.12 | ITC4 | A
IT | ITC46 |  | IT03160129000524 | DP01615701_PALOSCO | 45.5837 | 9.8319 | 8000 | 6605 | NO | 41.2812 | 0 | 0 | 0 | 239.4312 | 1436.5875 | ITC4 | A
IT | ITC46 |  | IT03160129000527 | DP01616801_PONTE_NOSSA | 45.856 | 9.8805 | 10000 | 9004 | NO | 56.275 | 0 | 0 | 0 | 326.395 | 1958.37 | ITC4 | A
IT | ITC46 |  | IT03160129000529 | DP01617801_RANICA | 45.7151 | 9.7259 | 250000 | 106306 | YES | 664.4125 | 2126.12 | 1594.59 | 3189.18 | 3853.5925 | 23121.555 | ITC4 | A
IT | ITC46 |  | IT03160128000129 | DP01618701_ROVETTA | 45.8696 | 9.9721 | 10000 | 5887 | NO | 36.7938 | 0 | 0 | 0 | 213.4038 | 1280.4225 | ITC4 | C
IT | ITC46 |  | IT03160128000134 | DP01619701_SELVINO | 45.7969 | 9.7495 | 12000 | 8673 | NO | 54.2063 | 0 | 0 | 0 | 314.3963 | 1886.3775 | ITC4 | B
IT | ITC46 |  | IT03160128000136 | DP01620801_STROZZA | 45.7791 | 9.5796 | 36000 | 16169 | NO | 101.0562 | 0 | 0 | 0 | 586.1262 | 3516.7575 | ITC4 | B
IT | ITC46 |  | IT03160128000137 | DP01621201_TELGATE | 45.6181 | 9.8615 | 11000 | 7448 | NO | 46.55 | 0 | 0 | 0 | 269.99 | 1619.94 | ITC4 | B
IT | ITC46 |  | IT03160128000138 | DP01621801_TRESCORE_BALNEARIO | 45.6815 | 9.8434 | 50086 | 40300 | NO | 251.875 | 0 | 0 | 0 | 1460.875 | 8765.25 | ITC4 | B
IT | ITC46 |  | IT03160128000141 | DP01622401_VALBREMBO | 45.7202 | 9.5967 | 77000 | 46371 | NO | 289.8188 | 0 | 0 | 0 | 1680.9488 | 10085.6925 | ITC4 | B
IT | ITC46 |  | IT03160128000142 | DP01624101_VILLA_D_OGNA | 45.8966 | 9.9224 | 11400 | 10504 | NO | 65.65 | 0 | 0 | 0 | 380.77 | 2284.62 | ITC4 | A
IT | ITC47 |  | IT03Q150000064 | DP01700801_AZZANO_MELLA | 45.4505 | 10.1132 | 5000 | 3040 | NO | 19 | 0 | 0 | 0 | 110.2 | 661.2 | ITC4 | B
IT | ITC47 |  | IT03160128000146 | DP01700901_BAGNOLO_MELLA | 45.4204 | 10.18 | 20500 | 13147 | NO | 82.1688 | 0 | 0 | 0 | 476.5787 | 2859.4725 | ITC4 | A
IT | ITC47 |  | IT03160128000149 | DP01701401_BEDIZZOLE_PONTENOVE | 45.4946 | 10.4049 | 12000 | 10690 | NO | 66.8125 | 0 | 0 | 0 | 387.5125 | 2325.075 | ITC4 | C
IT | ITC47 |  | IT03Q150000069 | DP01702007_BORGO_S_GIACOMO_NUOVO | 45.3488 | 9.9932 | 8200 | 5225 | NO | 32.6562 | 0 | 0 | 0 | 189.4062 | 1136.4375 | ITC4 | B
IT | ITC47 |  | IT03160128000156 | DP01702101_BORGOSATOLLO | 45.4704 | 10.2285 | 10000 | 8481 | NO | 53.0063 | 0 | 0 | 0 | 307.4362 | 1844.6175 | ITC4 | B
IT | ITC47 |  | IT03160128000160 | DP01702302_BOTTICINO_SERA | 45.525 | 10.2996 | 10000 | 7061 | NO | 44.1313 | 0 | 0 | 0 | 255.9613 | 1535.7675 | ITC4 | B
IT | ITC47 |  | IT03160129000531 | DP01702901_BRESCIA_VERZIANO | 45.4976 | 10.1771 | 296000 | 265180 | YES | 1657.375 | 5303.6 | 3977.7 | 7955.4 | 9612.775 | 57676.65 | ITC4 | A
IT | ITC47 |  | IT03160129000533 | DP01703201_CALCINATO_PRATI | 45.4468 | 10.4147 | 8260 | 6757 | NO | 42.2313 | 0 | 0 | 0 | 244.9412 | 1469.6475 | ITC4 | B
IT | ITC47 |  | IT03160129000543 | DP01704101_CASTELCOVATI | 45.4929 | 9.9363 | 5000 | 6707 | NO | 41.9188 | 0 | 0 | 0 | 243.1287 | 1458.7725 | ITC4 | B
IT | ITC4B |  | IT03160129000757 | DP02006602_VIADANA | 44.9388 | 10.5084 | 13000 | 16540 | NO | 103.375 | 0 | 0 | 0 | 599.575 | 3597.45 | ITC4 | A
IT | ITC43 |  | IT03160129000763 | DP09700401_BALLABIO | 45.8856 | 9.4261 | 13300 | 6627 | NO | 41.4188 | 0 | 0 | 0 | 240.2287 | 1441.3725 | ITC4 | A
IT | ITC43 |  | IT03160129000764 | DP09700701_BARZIO | 45.9332 | 9.4604 | 24000 | 12761 | NO | 79.7563 | 0 | 0 | 0 | 462.5863 | 2775.5175 | ITC4 | B
IT | ITC43 |  | IT03Q11000000691 | DP09700804_BELLANO_VIA_PER_COLICO | 46.0502 | 9.3091 | 8000 | 4906 | NO | 30.6625 | 0 | 0 | 0 | 177.8425 | 1067.055 | ITC4 | B
IT | ITC43 |  | IT03160129000769 | DP09701204_CALCO_TOFFO | 45.7299 | 9.446 | 38000 | 28370 | NO | 177.3125 | 0 | 0 | 0 | 1028.4125 | 6170.475 | ITC4 | B
IT | ITC43 |  | IT03160129000770 | DP09701301_CALOLZIOCORTE | 45.786 | 9.4352 | 40000 | 31145 | NO | 194.6562 | 0 | 0 | 0 | 1129.0062 | 6774.0375 | ITC4 | A
IT | ITC47 |  | IT03160129000544 | DP01704301_CASTENEDOLO | 45.4552 | 10.278 | 14000 | 11220 | NO | 70.125 | 0 | 0 | 0 | 406.725 | 2440.35 | ITC4 | C
IT | ITC47 |  | IT03160129000545 | DP01704501_CASTREZZATO | 45.5016 | 9.9824 | 7129 | 7089 | NO | 44.3062 | 0 | 0 | 0 | 256.9762 | 1541.8575 | ITC4 | C
IT | ITC47 |  | IT03160129000550 | DP01705201_CHIARI_SETTE_CANTONI | 45.5227 | 9.9376 | 30000 | 18423 | NO | 115.1438 | 0 | 0 | 0 | 667.8338 | 4007.0025 | ITC4 | C
IT | ITC47 |  | IT03160129000556 | DP01706301_CORTENO_GOLGI_S_PIETRO | 46.1597 | 10.1821 | 14000 | 17033 | NO | 106.4563 | 0 | 0 | 0 | 617.4462 | 3704.6775 | ITC4 | C
IT | ITC47 |  | IT03Q11000000211 | DP01706302_CORTENO_GOLGI_SANTICOLO | 46.1674 | 10.2615 | 5000 | 2811 | NO | 17.5688 | 0 | 0 | 0 | 101.8988 | 611.3925 | ITC4 | C
IT | ITC47 |  | IT03Q90000001499 | DP01707001_ESINE | 45.9246 | 10.2376 | 40000 | 29803 | NO | 186.2687 | 0 | 0 | 0 | 1080.3587 | 6482.1525 | ITC4 | B
IT | ITC47 |  | IT03160129000558 | DP01707201_FLERO | 45.477 | 10.1744 | 18000 | 11522 | NO | 72.0125 | 0 | 0 | 0 | 417.6725 | 2506.035 | ITC4 | B
IT | ITC47 |  | IT03Q150000120 | DP01707301_GAMBARA | 45.2516 | 10.3053 | 5500 | 4626 | NO | 28.9125 | 0 | 0 | 0 | 167.6925 | 1006.155 | ITC4 | B
IT | ITC47 |  | IT03160129000560 | DP01707701_GAVARDO | 45.578 | 10.4399 | 10000 | 13279 | NO | 82.9938 | 0 | 0 | 0 | 481.3637 | 2888.1825 | ITC4 | A
IT | ITC47 |  | IT03160129000561 | DP01707801_GHEDI | 45.392 | 10.2883 | 20000 | 19065 | NO | 119.1562 | 0 | 0 | 0 | 691.1063 | 4146.6375 | ITC4 | B
IT | ITC47 |  | IT03Q150000121 | DP01708001_GOTTOLENGO | 45.2863 | 10.2722 | 6000 | 5737 | NO | 35.8563 | 0 | 0 | 0 | 207.9663 | 1247.7975 | ITC4 | B
IT | ITC47 |  | IT03Q13000000212 | DP01708807_LENO_CAPOLUOGO | 45.3575 | 10.1979 | 5167 | 2289 | NO | 14.3063 | 0 | 0 | 0 | 82.9762 | 497.8575 | ITC4 | C
IT | ITC47 |  | IT03160129000571 | DP01709204_LONATO_CAMPAGNA | 45.4617 | 10.4703 | 8000 | 5825 | NO | 36.4062 | 0 | 0 | 0 | 211.1562 | 1266.9375 | ITC4 | B
IT | ITC47 |  | IT03160129000574 | DP01710301_MANERBIO | 45.3536 | 10.1531 | 40000 | 18812 | NO | 117.575 | 0 | 0 | 0 | 681.935 | 4091.61 | ITC4 | B
IT | ITC47 |  | IT03160129000576 | DP01710702_MAZZANO_CILIVERGHE | 45.4851 | 10.3432 | 10000 | 9226 | NO | 57.6625 | 0 | 0 | 0 | 334.4425 | 2006.655 | ITC4 | C
IT | ITC47 |  | IT03160129000577 | DP01711301_MONTICHIARI | 45.3997 | 10.389 | 40000 | 18822 | NO | 117.6375 | 0 | 0 | 0 | 682.2975 | 4093.785 | ITC4 | A
IT | ITC47 |  | IT03160129000578 | DP01711401_MONTIRONE | 45.4345 | 10.2413 | 6000 | 4953 | NO | 30.9563 | 0 | 0 | 0 | 179.5462 | 1077.2775 | ITC4 | C
IT | ITC47 |  | IT03160129000580 | DP01711701_NAVE | 45.5801 | 10.2701 | 6000 | 8854 | NO | 55.3375 | 0 | 0 | 0 | 320.9575 | 1925.745 | ITC4 | A
IT | ITC47 |  | IT03160129000583 | DP01712504_ORZINUOVI_LAME | 45.3936 | 9.9097 | 13000 | 10734 | NO | 67.0875 | 0 | 0 | 0 | 389.1075 | 2334.645 | ITC4 | B
IT | ITC47 |  | IT03Q150000172 | DP01712601_ORZIVECCHI | 45.4159 | 9.963 | 6000 | 2728 | NO | 17.05 | 0 | 0 | 0 | 98.89 | 593.34 | ITC4 | B
IT | ITC47 |  | IT03160129000587 | DP01713301_PALAZZOLO_SULL_OGLIO | 45.5856 | 9.8714 | 40000 | 31236 | NO | 195.225 | 0 | 0 | 0 | 1132.305 | 6793.83 | ITC4 | B
IT | ITC47 |  | IT03160129000588 | DP01713401_PARATICO | 45.6507 | 9.9388 | 70000 | 111606 | NO | 697.5375 | 0 | 0 | 0 | 4045.7175 | 24274.305 | ITC4 | B
IT | ITC47 |  | IT03160129000591 | DP01714901_PONTEVICO | 45.2646 | 10.0931 | 8000 | 7157 | NO | 44.7312 | 0 | 0 | 0 | 259.4412 | 1556.6475 | ITC4 | B
IT | ITC47 |  | IT03160129000592 | DP01715001_PONTOGLIO | 45.5639 | 9.8549 | 6000 | 7038 | NO | 43.9875 | 0 | 0 | 0 | 255.1275 | 1530.765 | ITC4 | B
IT | ITC47 |  | IT03160129000596 | DP01715901_QUINZANO_D_OGLIO | 45.3073 | 10.0128 | 6000 | 6411 | NO | 40.0688 | 0 | 0 | 0 | 232.3987 | 1394.3925 | ITC4 | B
IT | ITC47 |  | IT03Q150000186 | DP01716602_ROVATO_INTERCOMUNALE | 45.5327 | 10.0385 | 90000 | 66215 | YES | 413.8438 | 1324.3 | 993.225 | 1986.45 | 2400.2937 | 14401.7625 | ITC4 | C
IT | ITC47 |  | IT03Q13000000439 | DP01716702_RUDIANO_NUOVO | 45.4835 | 9.8811 | 12000 | 5663 | NO | 35.3938 | 0 | 0 | 0 | 205.2837 | 1231.7025 | ITC4 | B
IT | ITC47 |  | IT03160129000606 | DP01716801_SABBIO_CHIESE | 45.6485 | 10.4396 | 26000 | 22625 | NO | 141.4062 | 0 | 0 | 0 | 820.1562 | 4920.9375 | ITC4 | C
IT | ITC47 |  | IT03Q150000201 | DP01718602_TORBOLE_CASAGLIA_INTERCOMUNALE | 45.4864 | 10.1164 | 93000 | 63539 | YES | 397.1188 | 1270.78 | 953.085 | 1906.17 | 2303.2888 | 13819.7325 | ITC4 | C
IT | ITC47 |  | IT03160129000612 | DP01718801_TRAVAGLIATO | 45.5101 | 10.0926 | 20000 | 17355 | NO | 108.4688 | 0 | 0 | 0 | 629.1187 | 3774.7125 | ITC4 | B
IT | ITC47 |  | IT03Q13000000441 | DP01718901_TREMOSINE_LARGO_DEI_MINATORI | 45.7708 | 10.7654 | 18750 | 15420 | NO | 96.375 | 0 | 0 | 0 | 558.975 | 3353.85 | ITC4 | B
IT | ITC47 |  | IT03160129000613 | DP01719001_TRENZANO | 45.4713 | 10.0111 | 5516 | 7699 | NO | 48.1188 | 0 | 0 | 0 | 279.0888 | 1674.5325 | ITC4 | B
IT | ITC47 |  | IT03160129000615 | DP01719501_VEROLANUOVA | 45.3214 | 10.0792 | 10000 | 7225 | NO | 45.1562 | 0 | 0 | 0 | 261.9062 | 1571.4375 | ITC4 | A
IT | ITC47 |  | IT03160129000618 | DP01719801_VEZZA_D_OGLIO | 46.2305 | 10.3793 | 36333 | 32026 | NO | 200.1625 | 0 | 0 | 0 | 1160.9425 | 6965.655 | ITC4 | C
IT | ITC47 |  | IT03160129000619 | DP01720101_VILLANUOVA_SUL_CLISI | 45.601 | 10.4452 | 8000 | 5602 | NO | 35.0125 | 0 | 0 | 0 | 203.0725 | 1218.435 | ITC4 | A
IT | ITC48 |  | IT03Q11000000674 | DP01800516_ARENA_PO_ZAPPELLONE | 45.0844 | 9.4158 | 8500 | 4533 | NO | 28.3313 | 0 | 0 | 0 | 164.3212 | 985.9275 | ITC4 | C
IT | ITC48 |  | IT03160129000625 | DP01801301_BELGIOIOSO | 45.1498 | 9.3171 | 5700 | 9069 | NO | 56.6813 | 0 | 0 | 0 | 328.7513 | 1972.5075 | ITC4 | B
IT | ITC48 |  | IT03160129000628 | DP01802401_BRONI_CAPOLUOGO | 45.0935 | 9.2673 | 52000 | 18097 | NO | 113.1063 | 0 | 0 | 0 | 656.0163 | 3936.0975 | ITC4 | C
IT | ITC48 |  | IT03160129000631 | DP01803501_CASSOLNOVO | 45.3665 | 8.8264 | 9000 | 7590 | NO | 47.4375 | 0 | 0 | 0 | 275.1375 | 1650.825 | ITC4 | C
IT | ITC48 |  | IT03160129000632 | DP01803701_CASTEGGIO | 45.0239 | 9.1201 | 47000 | 39866 | NO | 249.1625 | 0 | 0 | 0 | 1445.1425 | 8670.855 | ITC4 | B
IT | ITC48 |  | IT03160129000633 | DP01804101_CAVA_MANARA | 45.1445 | 9.113 | 15000 | 8128 | NO | 50.8 | 0 | 0 | 0 | 294.64 | 1767.84 | ITC4 | A
IT | ITC48 |  | IT03160129000639 | DP01804801_CHIGNOLO_PO | 45.149 | 9.4744 | 6500 | 3271 | NO | 20.4438 | 0 | 0 | 0 | 118.5737 | 711.4425 | ITC4 | B
IT | ITC48 |  | IT03160129000640 | DP01805001_CILAVEGNA | 45.3127 | 8.7527 | 9300 | 6384 | NO | 39.9 | 0 | 0 | 0 | 231.42 | 1388.52 | ITC4 | A
IT | ITC48 |  | IT03160129000642 | DP01806101_DORNO | 45.1458 | 8.9429 | 5900 | 5764 | NO | 36.025 | 0 | 0 | 0 | 208.945 | 1253.67 | ITC4 | B
IT | ITC48 |  | IT03160129000643 | DP01806801_GAMBOLO_CAPOLUOGO | 45.2484 | 8.8641 | 12000 | 9430 | NO | 58.9375 | 0 | 0 | 0 | 341.8375 | 2051.025 | ITC4 | B
IT | ITC48 |  | IT03160129000644 | DP01806901_GARLASCO | 45.1804 | 8.9213 | 20500 | 16868 | NO | 105.425 | 0 | 0 | 0 | 611.465 | 3668.79 | ITC4 | C
IT | ITC48 |  | IT03160129000648 | DP01807801_LANDRIANO | 45.305 | 9.2631 | 6150 | 6055 | NO | 37.8438 | 0 | 0 | 0 | 219.4938 | 1316.9625 | ITC4 | B
IT | ITC48 |  | IT03Q11000000675 | DP01808102_LINAROLO | 45.1455 | 9.2665 | 5000 | 4232 | NO | 26.45 | 0 | 0 | 0 | 153.41 | 920.46 | ITC4 | C
IT | ITC48 |  | IT03160129000651 | DP01808801_MEDE | 45.0893 | 8.7334 | 21250 | 23531 | NO | 147.0687 | 0 | 0 | 0 | 852.9987 | 5117.9925 | ITC4 | A
IT | ITC48 |  | IT03160129000654 | DP01810201_MORTARA | 45.2448 | 8.7516 | 86000 | 20329 | NO | 127.0562 | 0 | 0 | 0 | 736.9262 | 4421.5575 | ITC4 | A
IT | ITC48 |  | IT03160129000655 | DP01811001_PAVIA | 45.1775 | 9.179 | 130000 | 118999 | YES | 743.7438 | 2379.98 | 1784.985 | 3569.97 | 4313.7137 | 25882.2825 | ITC4 | A
IT | ITC48 |  | IT03Q11000000676 | DP01812205_RIVANAZZANO_TERME_SALICE_TERME_DI_GODIASCO | 44.9208 | 9.0235 | 8250 | 2391 | NO | 14.9438 | 0 | 0 | 0 | 86.6737 | 520.0425 | ITC4 | B
IT | ITC48 |  | IT03160129000658 | DP01812301_ROBBIO | 45.2839 | 8.612 | 23100 | 17881 | NO | 111.7563 | 0 | 0 | 0 | 648.1862 | 3889.1175 | ITC4 | B
IT | ITC48 |  | IT03160129000659 | DP01813801_SANNAZZARO_DE_BURGONDI | 45.0974 | 8.9117 | 9000 | 8812 | NO | 55.075 | 0 | 0 | 0 | 319.435 | 1916.61 | ITC4 | A
IT | ITC48 |  | IT03160129000660 | DP01813902_S_CRISTINA_E_BISSONE | 45.1528 | 9.3978 | 6000 | 4010 | NO | 25.0625 | 0 | 0 | 0 | 145.3625 | 872.175 | ITC4 | B
IT | ITC48 |  | IT03160129000661 | DP01815001_SIZIANO | 45.3186 | 9.2083 | 9500 | 6749 | NO | 42.1812 | 0 | 0 | 0 | 244.6512 | 1467.9075 | ITC4 | B
IT | ITC48 |  | IT03160129000662 | DP01815301_STRADELLA | 45.0851 | 9.291 | 38500 | 24202 | NO | 151.2625 | 0 | 0 | 0 | 877.3225 | 5263.935 | ITC4 | A
IT | ITC48 |  | IT03Q170000205 | DP01817603_VIDIGULFO | 45.2792 | 9.2417 | 14500 | 8269 | NO | 51.6813 | 0 | 0 | 0 | 299.7513 | 1798.5075 | ITC4 | C
IT | ITC4A |  | IT03Q90000001115 | DP01909801_SORESINA | 45.2762 | 9.8461 | 14000 | 9405 | NO | 58.7812 | 0 | 0 | 0 | 340.9312 | 2045.5875 | ITC4 | C
IT | ITC4A |  | IT03Q11000000680 | DP01909901_SOSPIRO | 45.0999 | 10.1566 | 6560 | 2987 | NO | 18.6687 | 0 | 0 | 0 | 108.2787 | 649.6725 | ITC4 | B
IT | ITC4A |  | IT03160129000694 | DP01910201_SPINO_D_ADDA | 45.3957 | 9.4856 | 9000 | 7169 | NO | 44.8062 | 0 | 0 | 0 | 259.8762 | 1559.2575 | ITC4 | A
IT | ITC4B |  | IT03160129000697 | DP02000201_ASOLA | 45.2162 | 10.4159 | 10000 | 6891 | NO | 43.0688 | 0 | 0 | 0 | 249.7987 | 1498.7925 | ITC4 | A
IT | ITC4B |  | IT03160129000702 | DP02000306_BAGNOLO_S_VITO | 45.0929 | 10.8741 | 6000 | 4920 | NO | 30.75 | 0 | 0 | 0 | 178.35 | 1070.1 | ITC4 | B
IT | ITC4B |  | IT03160129000707 | DP02000701_BOZZOLO | 45.1085 | 10.4895 | 6500 | 4104 | NO | 25.65 | 0 | 0 | 0 | 148.77 | 892.62 | ITC4 | B
IT | ITC4B |  | IT03160129000709 | DP02000802_CANNETO_SULL_OGLIO_LOC_BREDA | 45.1451 | 10.3869 | 5000 | 4264 | NO | 26.65 | 0 | 0 | 0 | 154.57 | 927.42 | ITC4 | B
IT | ITC4B |  | IT03160129000714 | DP02001502_CASTEL_GOFFREDO_VILLA | 45.2809 | 10.4453 | 18000 | 14726 | NO | 92.0375 | 0 | 0 | 0 | 533.8175 | 3202.905 | ITC4 | C
IT | ITC4B |  | IT03160129000715 | DP02001601_CASTELLUCCHIO | 45.1488 | 10.6577 | 5500 | 4070 | NO | 25.4375 | 0 | 0 | 0 | 147.5375 | 885.225 | ITC4 | B
IT | ITC4B |  | IT03160129000716 | DP02001701_CASTIGLIONE_DELLE_STIVIERE | 45.3677 | 10.5014 | 70000 | 52748 | NO | 329.675 | 0 | 0 | 0 | 1912.115 | 11472.69 | ITC4 | A
IT | ITC4B |  | IT03160129000720 | DP02002601_GOITO | 45.2417 | 10.6659 | 8000 | 7952 | NO | 49.7 | 0 | 0 | 0 | 288.26 | 1729.56 | ITC4 | B
IT | ITC4B |  | IT03Q190000003 | DP02002702_GONZAGA | 44.9519 | 10.8359 | 8500 | 8217 | NOT KNOWN | 51.3562 | 0 | 0 | 0 | 297.8662 | 1787.1975 | ITC4 | B
IT | ITC4B |  | IT03160129000722 | DP02002801_GUIDIZZOLO | 45.283 | 10.5908 | 17500 | 10723 | NO | 67.0187 | 0 | 0 | 0 | 388.7088 | 2332.2525 | ITC4 | C
IT | ITC4B |  | IT03160129000723 | DP02003001_MANTOVA | 45.1382 | 10.8043 | 100000 | 87852 | YES | 549.075 | 1757.04 | 1317.78 | 2635.56 | 3184.635 | 19107.81 | ITC4 | B
IT | ITC4B |  | IT03Q11000000683 | DP02003302_MARMIROLO_STR_SOAVE | 45.2156 | 10.7463 | 6600 | 5743 | NO | 35.8938 | 0 | 0 | 0 | 208.1838 | 1249.1025 | ITC4 | B
IT | ITC4B |  | IT03160129000729 | DP02003501_MOGLIA | 44.9435 | 10.9134 | 11667 | 3326 | NO | 20.7875 | 0 | 0 | 0 | 120.5675 | 723.405 | ITC4 | B
IT | ITC4B |  | IT03Q11000000685 | DP02003801_OSTIGLIA | 45.0835 | 11.1382 | 6200 | 7158 | NO | 44.7375 | 0 | 0 | 0 | 259.4775 | 1556.865 | ITC4 | B
IT | ITC4B |  | IT03160129000734 | DP02003901_PEGOGNAGA | 45.0008 | 10.8673 | 8000 | 5600 | NO | 35 | 0 | 0 | 0 | 203 | 1218 | ITC4 | B
IT | ITC4B |  | IT03160129000736 | DP02004201_POGGIO_RUSCO | 44.9734 | 11.1243 | 5500 | 6668 | NO | 41.675 | 0 | 0 | 0 | 241.715 | 1450.29 | ITC4 | A
IT | ITC4B |  | IT03Q13000000488 | DP02004302_POMPONESCO | 44.9367 | 10.5976 | 9500 | 3056 | NO | 19.1 | 0 | 0 | 0 | 110.78 | 664.68 | ITC4 | A
IT | ITC4B |  | IT03160129000737 | DP02004501_PORTO_MANTOVANO_FAVORITA | 45.1842 | 10.7953 | 11000 | 9277 | NO | 57.9812 | 0 | 0 | 0 | 336.2912 | 2017.7475 | ITC4 | A
IT | ITC4B |  | IT03Q11000000686 | DP02004503_PORTO_MANTOVANO_MANTOVANELLA | 45.1869 | 10.7731 | 7600 | 6532 | NO | 40.825 | 0 | 0 | 0 | 236.785 | 1420.71 | ITC4 | A
IT | ITC4B |  | IT03Q11000000688 | DP02004701_QUISTELLO | 44.9972 | 10.9844 | 7000 | 5629 | NO | 35.1812 | 0 | 0 | 0 | 204.0512 | 1224.3075 | ITC4 | B
IT | ITC4B |  | IT03160129000740 | DP02004801_REDONDESCO | 45.1516 | 10.5295 | 7800 | 7497 | NO | 46.8562 | 0 | 0 | 0 | 271.7662 | 1630.5975 | ITC4 | C
IT | ITC48 |  | IT03160129000669 | DP01817701_VIGEVANO | 45.3206 | 8.8949 | 86500 | 73516 | NO | 459.475 | 0 | 0 | 0 | 2664.955 | 15989.73 | ITC4 | B
IT | ITC48 |  | IT03160129000670 | DP01818001_VILLANTERIO | 45.212 | 9.3476 | 9300 | 5502 | NO | 34.3875 | 0 | 0 | 0 | 199.4475 | 1196.685 | ITC4 | C
IT | ITC48 |  | IT03160129000671 | DP01818201_VOGHERA | 45.0093 | 8.9854 | 70000 | 49047 | NO | 306.5437 | 0 | 0 | 0 | 1777.9537 | 10667.7225 | ITC4 | C
IT | ITC4A |  | IT03160129000673 | DP01900501_SERIO_2 | 45.3476 | 9.5971 | 62000 | 34290 | NO | 214.3125 | 0 | 0 | 0 | 1243.0125 | 7458.075 | ITC4 | C
IT | ITC4A |  | IT03160129000674 | DP01901602_CASALBUTTANO | 45.2417 | 9.9765 | 16000 | 10572 | NO | 66.075 | 0 | 0 | 0 | 383.235 | 2299.41 | ITC4 | C
IT | ITC4A |  | IT03160129000676 | DP01902101_CASALMAGGIORE_VICOMOSCANO | 44.9853 | 10.4514 | 40000 | 23170 | NO | 144.8125 | 0 | 0 | 0 | 839.9125 | 5039.475 | ITC4 | C
IT | ITC4A |  | IT03160129000677 | DP01903501_SERIO_1 | 45.3465 | 9.694 | 138000 | 113214 | YES | 707.5875 | 2264.28 | 1698.21 | 3396.42 | 4104.0075 | 24624.045 | ITC4 | A
IT | ITC4A |  | IT03160129000678 | DP01903601_CREMONA | 45.1232 | 10.0271 | 180000 | 108830 | YES | 680.1875 | 2176.6 | 1632.45 | 3264.9 | 3945.0875 | 23670.525 | ITC4 | A
IT | ITC4A |  | IT03Q90000001638 | DP01905901_MONTODINE | 45.2791 | 9.7008 | 9488 | 4777 | NO | 29.8563 | 0 | 0 | 0 | 173.1663 | 1038.9975 | ITC4 | B
IT | ITC4A |  | IT03160129000685 | DP01907101_PIADENA | 45.131 | 10.3819 | 7400 | 3682 | NO | 23.0125 | 0 | 0 | 0 | 133.4725 | 800.835 | ITC4 | B
IT | ITC4A |  | IT03160129000686 | DP01907601_PIZZIGHETTONE | 45.1795 | 9.7837 | 8400 | 8217 | NO | 51.3562 | 0 | 0 | 0 | 297.8662 | 1787.1975 | ITC4 | B
IT | ITC4A |  | IT03160129000687 | DP01908401_RIVOLTA_D_ADDA | 45.4637 | 9.5036 | 13500 | 8498 | NO | 53.1125 | 0 | 0 | 0 | 308.0525 | 1848.315 | ITC4 | B
IT | ITC4A |  | IT03160129000693 | DP01909701_SONCINO | 45.3905 | 9.8735 | 8266 | 8071 | NO | 50.4438 | 0 | 0 | 0 | 292.5738 | 1755.4425 | ITC4 | B
IT | ITC4B |  | IT03160129000749 | DP02005501_S_BENEDETTO_PO | 45.0458 | 10.9443 | 7000 | 4612 | NO | 28.825 | 0 | 0 | 0 | 167.185 | 1003.11 | ITC4 | B
IT | ITC4B |  | IT03160129000753 | DP02006101_SERMIDE | 44.9964 | 11.282 | 10000 | 4947 | NO | 30.9188 | 0 | 0 | 0 | 179.3287 | 1075.9725 | ITC4 | B
IT | ITC4B |  | IT03160129000755 | DP02006501_SUZZARA | 45.0054 | 10.7449 | 13500 | 16650 | NO | 104.0625 | 0 | 0 | 0 | 603.5625 | 3621.375 | ITC4 | B
IT | ITC4B |  | IT03160129000756 | DP02006502_SUZZARA_BRUSATASSO | 44.9841 | 10.7735 | 5400 | 2722 | NO | 17.0125 | 0 | 0 | 0 | 98.6725 | 592.035 | ITC4 | B
IT | ITC47 |  | IT03160129000540 | DP01703901_CARPENEDOLO_GARIBALDI | 45.3511 | 10.4284 | 13000 | 14615 | NO | 91.3438 | 0 | 0 | 0 | 529.7937 | 3178.7625 | ITC4 | A
IT | ITC43 |  | IT03160129000772 | DP09702301_COLICO_MONTEGGIOLO | 46.1419 | 9.3822 | 10000 | 11233 | NO | 70.2062 | 0 | 0 | 0 | 407.1962 | 2443.1775 | ITC4 | A
IT | ITC43 |  | IT03160129000774 | DP09703001_DERVIO | 46.073 | 9.2979 | 7800 | 6147 | NO | 38.4188 | 0 | 0 | 0 | 222.8288 | 1336.9725 | ITC4 | A
IT | ITC43 |  | IT03160129000781 | DP09704201_LECCO | 45.8399 | 9.4015 | 67000 | 61864 | NO | 386.65 | 0 | 0 | 0 | 2242.57 | 13455.42 | ITC4 | A
IT | ITC43 |  | IT03160129000782 | DP09704401_LOMAGNA | 45.6644 | 9.3663 | 40800 | 33811 | NO | 211.3188 | 0 | 0 | 0 | 1225.6488 | 7353.8925 | ITC4 | A
IT | ITC43 |  | IT03160129000783 | DP09704601_MANDELLO_DEL_LARIO | 45.915 | 9.3163 | 20000 | 21807 | NO | 136.2938 | 0 | 0 | 0 | 790.5038 | 4743.0225 | ITC4 | A
IT | ITC43 |  | IT03160129000788 | DP09705601_NIBIONNO | 45.7466 | 9.2512 | 30000 | 42103 | NO | 263.1438 | 0 | 0 | 0 | 1526.2338 | 9157.4025 | ITC4 | B
IT | ITC43 |  | IT03160129000789 | DP09705901_OLGINATE | 45.7936 | 9.4224 | 29000 | 27570 | NO | 172.3125 | 0 | 0 | 0 | 999.4125 | 5996.475 | ITC4 | A
IT | ITC43 |  | IT03160129000790 | DP09706101_OSNAGO | 45.664 | 9.3819 | 36340 | 35826 | NO | 223.9125 | 0 | 0 | 0 | 1298.6925 | 7792.155 | ITC4 | B
IT | ITC43 |  | IT03Q170000027 | DP09706701_PERLEDO_OLIVEDO | 46.0141 | 9.2886 | 5000 | 1861 | NO | 11.6313 | 0 | 0 | 0 | 67.4613 | 404.7675 | ITC4 | A
IT | ITC43 |  | IT03160129000794 | DP09707901_TACENO | 46.0207 | 9.3587 | 26000 | 20015 | NO | 125.0938 | 0 | 0 | 0 | 725.5437 | 4353.2625 | ITC4 | B
IT | ITC49 |  | IT03160129000812 | DP09802902_GUARDAMIGLIO | 45.1118 | 9.6903 | 5000 | 3284 | NO | 20.525 | 0 | 0 | 0 | 119.045 | 714.27 | ITC4 | A
IT | ITC49 |  | IT03160129000813 | DP09803102_LODI | 45.3052 | 9.5204 | 60000 | 51608 | NO | 322.55 | 0 | 0 | 0 | 1870.79 | 11224.74 | ITC4 | B
IT | ITC49 |  | IT03Q13000000118 | DP09804501_PIEVE_FISSIRAGA_INTERCOMUNALE | 45.2582 | 9.4687 | 13000 | 8231 | NO | 51.4438 | 0 | 0 | 0 | 298.3737 | 1790.2425 | ITC4 | C
IT | ITC49 |  | IT03160129000821 | DP09804601_SALERANO_SUL_LAMBRO | 45.3014 | 9.3819 | 34000 | 33927 | NO | 212.0438 | 0 | 0 | 0 | 1229.8537 | 7379.1225 | ITC4 | B
IT | ITC49 |  | IT03160129000822 | DP09804801_S_MARTINO_IN_STRADA | 45.2647 | 9.5364 | 6500 | 4078 | NO | 25.4875 | 0 | 0 | 0 | 147.8275 | 886.965 | ITC4 | B
IT | ITC49 |  | IT03160129000825 | DP09805001_S_ANGELO_LODIGIANO | 45.2425 | 9.421 | 23770 | 20851 | NO | 130.3187 | 0 | 0 | 0 | 755.8487 | 4535.0925 | ITC4 | B
IT | ITC49 |  | IT03160129000827 | DP09806101_ZELO_BUON_PERSICO | 45.4056 | 9.4428 | 8000 | 7699 | NO | 48.1188 | 0 | 0 | 0 | 279.0888 | 1674.5325 | ITC4 | B
IT | ITC11 |  | IT01000000000063 | FELETTO_RIVAROLO | 45.2857 | 7.7651 | 60290 | 54820 | NO | 342.625 | 0 | 0 | 0 | 1987.225 | 11923.35 | ITC1 | C
IT | ITC11 |  | IT01000000000065 | STRAMBINO_FRAZ_CROTTE | 45.3808 | 7.9136 | 10000 | 8964 | NO | 56.025 | 0 | 0 | 0 | 324.945 | 1949.67 | ITC1 | C
IT | ITC11 |  | IT01Q90000002531 | OULX_GAD | 45.0473 | 6.8553 | 10088 | 13213 | NO | 82.5812 | 0 | 0 | 0 | 478.9712 | 2873.8275 | ITC1 | C
IT | ITC11 |  | IT01Q90000001438 | CERES | 45.3161 | 7.3919 | 8000 | 2320 | NO | 14.5 | 0 | 0 | 0 | 84.1 | 504.6 | ITC1 | B
IT | ITC11 |  | IT01Q90000001437 | CESANA_TORINESE_BOUSSON | 44.9346 | 6.8142 | 9000 | 4851 | NO | 30.3187 | 0 | 0 | 0 | 175.8487 | 1055.0925 | ITC1 | C
IT | ITC11 |  | IT01Q90000001434 | VEROLENGO | 45.184 | 7.9702 | 5000 | 3477 | NO | 21.7312 | 0 | 0 | 0 | 126.0412 | 756.2475 | ITC1 | B
IT | ITC12 |  | IT01Q90000001433 | TRINO | 45.1949 | 8.3062 | 9000 | 5249 | NO | 32.8062 | 0 | 0 | 0 | 190.2762 | 1141.6575 | ITC1 | B
IT | ITC13 |  | IT01Q90000001432 | CERRIONE | 45.4671 | 8.0942 | 11000 | 10307 | NO | 64.4188 | 0 | 0 | 0 | 373.6288 | 2241.7725 | ITC1 | C
IT | ITC18 |  | IT01Q19000000001 | ALICE_BEL_COLLE | 44.714 | 8.449 | 10000 | 7301 | NOT KNOWN | 45.6313 | 0 | 0 | 0 | 264.6612 | 1587.9675 | ITC1 | C
IT | ITC16 |  | IT01000000000131 | CANOVE_DI_GOVONE | 44.7752 | 8.1057 | 240000 | 200175 | YES | 1251.0938 | 4003.5 | 3002.625 | 6005.25 | 7256.3438 | 43538.0625 | ITC1 | C
IT | ITC16 |  | IT01000000000130 | GARESSIO | 44.234 | 8.0162 | 21770 | 13872 | NO | 86.7 | 0 | 0 | 0 | 502.86 | 3017.16 | ITC1 | C
IT | ITC16 |  | IT01000000000128 | VILLANOVA_MONDOVI | 44.3479 | 7.7858 | 5000 | 4200 | NO | 26.25 | 0 | 0 | 0 | 152.25 | 913.5 | ITC1 | B
IT | ITC16 |  | IT01000000000127 | ROCCAFORTE | 44.3235 | 7.7492 | 5500 | 3500 | NO | 21.875 | 0 | 0 | 0 | 126.875 | 761.25 | ITC1 | B
IT | ITC16 |  | IT01000000000126 | DRONERO | 44.4661 | 7.3681 | 7000 | 5000 | NO | 31.25 | 0 | 0 | 0 | 181.25 | 1087.5 | ITC1 | A
IT | ITC16 |  | IT01000000000125 | CARAGLIO | 44.4107 | 7.4536 | 7000 | 3812 | NO | 23.825 | 0 | 0 | 0 | 138.185 | 829.11 | ITC1 | C
IT | ITC16 |  | IT01000000000145 | MORETTA | 44.7742 | 7.5355 | 5000 | 4000 | NO | 25 | 0 | 0 | 0 | 145 | 870 | ITC1 | B
IT | ITC16 |  | IT01000000000144 | RACCONIGI | 44.7792 | 7.6815 | 12000 | 8100 | NO | 50.625 | 0 | 0 | 0 | 293.625 | 1761.75 | ITC1 | B
IT | ITC17 |  | IT01000000000148 | ASTI | 44.8905 | 8.225 | 95000 | 85956 | NO | 537.225 | 0 | 0 | 0 | 3115.905 | 18695.43 | ITC1 | A
IT | ITC16 |  | IT01000000000133 | BRA_LA_BASSA | 44.6867 | 7.8568 | 45000 | 38409 | NO | 240.0563 | 0 | 0 | 0 | 1392.3262 | 8353.9575 | ITC1 | B
IT | ITC18 |  | IT01000000000167 | SALE | 44.9885 | 8.8135 | 5000 | 3055 | NO | 19.0938 | 0 | 0 | 0 | 110.7438 | 664.4625 | ITC1 | B
IT | ITC18 |  | IT01000000000165 | CASTELLAZZO_BORMIDA | 44.8516 | 8.5897 | 7000 | 2635 | NO | 16.4688 | 0 | 0 | 0 | 95.5187 | 573.1125 | ITC1 | B
IT | ITC18 |  | IT01000000000164 | BISTAGNO | 44.6534 | 8.3765 | 11000 | 11000 | NO | 68.75 | 0 | 0 | 0 | 398.75 | 2392.5 | ITC1 | B
IT | ITC16 |  | IT01000000000146 | BARGE | 44.7224 | 7.3675 | 15000 | 12152 | NO | 75.95 | 0 | 0 | 0 | 440.51 | 2643.06 | ITC1 | C
IT | ITC18 |  | IT01000000000158 | BASALUZZO | 44.7621 | 8.6805 | 40000 | 36466 | NO | 227.9125 | 0 | 0 | 0 | 1321.8925 | 7931.355 | ITC1 | C
IT | ITC16 |  | IT01000000000122 | PEVERAGNO | 44.3348 | 7.6236 | 5000 | 3472 | NO | 21.7 | 0 | 0 | 0 | 125.86 | 755.16 | ITC1 | A
IT | ITC15 |  | IT01000000000021 | OVEST_TICINO_CERANO | 45.401 | 8.8093 | 122000 | 88581 | YES | 553.6313 | 1771.62 | 1328.715 | 2657.43 | 3211.0612 | 19266.3675 | ITC1 | C
IT | ITC14 |  | IT01000000000010 | CANNOBBIO | 46.0662 | 8.6923 | 23500 | 18667 | NO | 116.6688 | 0 | 0 | 0 | 676.6787 | 4060.0725 | ITC1 | A
IT | ITC12 |  | IT01000000000031 | VERCELLI | 45.3158 | 8.4355 | 80000 | 56256 | NO | 351.6 | 0 | 0 | 0 | 2039.28 | 12235.68 | ITC1 | A
IT | ITC12 |  | IT01000000000030 | GATTINARA | 45.5992 | 8.3782 | 10000 | 9645 | NO | 60.2812 | 0 | 0 | 0 | 349.6312 | 2097.7875 | ITC1 | B
IT | ITC12 |  | IT01000000000028 | BORGOSESIA | 45.7098 | 8.289 | 5000 | 5000 | NO | 31.25 | 0 | 0 | 0 | 181.25 | 1087.5 | ITC1 | B
IT | ITC13 |  | IT01000000000027 | BIELLA_PONDERANO_BIELLA_SUD | 45.5413 | 8.0417 | 53000 | 13553 | NO | 84.7062 | 0 | 0 | 0 | 491.2962 | 2947.7775 | ITC1 | A
IT | ITC13 |  | IT01000000000026 | COSSATO_SPOLINA | 45.5444 | 8.1829 | 520000 | 197594 | YES | 1234.9625 | 3951.88 | 2963.91 | 5927.82 | 7162.7825 | 42976.695 | ITC1 | C
IT | ITC13 |  | IT01000000000025 | CORDAR_VALSESIA | 45.6548 | 8.3407 | 84000 | 61416 | YES | 383.85 | 1228.32 | 921.24 | 1842.48 | 2226.33 | 13357.98 | ITC1 | A
IT | ITC13 |  | IT01000000000024 | MASSAZZA | 45.4815 | 8.1745 | 37000 | 27831 | NO | 173.9437 | 0 | 0 | 0 | 1008.8737 | 6053.2425 | ITC1 | C
IT | ITC15 |  | IT01000000000022 | NOVARA | 45.4214 | 8.5968 | 190000 | 184763 | YES | 1154.7687 | 3695.26 | 2771.445 | 5542.89 | 6697.6587 | 40185.9525 | ITC1 | C
IT | ITC15 |  | IT01000000000020 | BELLINZAGO_NOVARESE | 45.5686 | 8.6717 | 36000 | 27855 | NO | 174.0938 | 0 | 0 | 0 | 1009.7437 | 6058.4625 | ITC1 | C
IT | ITC12 |  | IT01000000000019 | BASSA_VALSESIA | 45.547 | 8.4601 | 50000 | 44587 | NO | 278.6687 | 0 | 0 | 0 | 1616.2787 | 9697.6725 | ITC1 | A
IT | ITC15 |  | IT01000000000017 | BORGOMANERO_VIA_PIOVALE | 45.6882 | 8.4612 | 38000 | 21043 | NO | 131.5188 | 0 | 0 | 0 | 762.8087 | 4576.8525 | ITC1 | B
IT | ITC14 |  | IT01000000000015 | CUSIO_AGOGNA | 45.7207 | 8.4563 | 40000 | 13741 | NO | 85.8813 | 0 | 0 | 0 | 498.1113 | 2988.6675 | ITC1 | B
IT | ITC15 |  | IT01000000000014 | DORMELLETTO | 45.7449 | 8.5625 | 65000 | 54120 | NO | 338.25 | 0 | 0 | 0 | 1961.85 | 11771.1 | ITC1 | A
IT | ITC18 |  | IT01000000000168 | ALESSANDRIA_ORTI | 44.9381 | 8.7046 | 110000 | 58666 | YES | 366.6625 | 1173.32 | 879.99 | 1759.98 | 2126.6425 | 12759.855 | ITC1 | C
IT | ITC15 |  | IT01000000000023 | BORGOLAVEZZARO | 45.303 | 8.6991 | 9500 | 7174 | NO | 44.8375 | 0 | 0 | 0 | 260.0575 | 1560.345 | ITC1 | C
IT | ITC11 |  | IT01000000000043 | CASTIGLIONE | 45.1368 | 7.7977 | 3840000 | 1931129 | YES | 12069.5563 | 38622.58 | 28966.935 | 57933.87 | 70003.4263 | 420020.5575 | ITC1 | A
IT | ITC16 |  | IT01000000000061 | MONTANARO | 45.2214 | 7.8507 | 5300 | 3886 | NO | 24.2875 | 0 | 0 | 0 | 140.8675 | 845.205 | ITC1 | B
IT | ITC11 |  | IT01000000000060 | BALANGERO_MATHI_NOLE | 45.2271 | 7.5716 | 15000 | 17583 | NO | 109.8938 | 0 | 0 | 0 | 637.3838 | 3824.3025 | ITC1 | C
IT | ITC11 |  | IT01000000000059 | CALUSO_MAZZE | 45.2778 | 7.9545 | 20000 | 16568 | NO | 103.55 | 0 | 0 | 0 | 600.59 | 3603.54 | ITC1 | C
IT | ITC11 |  | IT01000000000057 | CERETTA_S_MAURIZIO | 45.1866 | 7.6076 | 42000 | 38611 | NO | 241.3188 | 0 | 0 | 0 | 1399.6488 | 8397.8925 | ITC1 | C
IT | ITC11 |  | IT01000000000056 | MONTALTO_DORA | 45.4814 | 7.8602 | 7000 | 5873 | NO | 36.7063 | 0 | 0 | 0 | 212.8963 | 1277.3775 | ITC1 | B
IT | ITC11 |  | IT01000000000055 | NONE | 44.9323 | 7.5558 | 7500 | 7886 | NO | 49.2875 | 0 | 0 | 0 | 285.8675 | 1715.205 | ITC1 | B
IT | ITC11 |  | IT01000000000054 | CHIVASSO | 45.1843 | 7.9209 | 60000 | 28487 | NO | 178.0438 | 0 | 0 | 0 | 1032.6537 | 6195.9225 | ITC1 | C
IT | ITC12 |  | IT01000000000032 | SANTHIA | 45.3639 | 8.189 | 10000 | 9516 | NO | 59.475 | 0 | 0 | 0 | 344.955 | 2069.73 | ITC1 | A
IT | ITC11 |  | IT01000000000045 | BRANDIZZO | 45.1792 | 7.8541 | 9000 | 8827 | NO | 55.1687 | 0 | 0 | 0 | 319.9787 | 1919.8725 | ITC1 | B
IT | ITC14 |  | IT01000000000009 | DOMODOSSOLA | 46.0925 | 8.2965 | 30000 | 22280 | NO | 139.25 | 0 | 0 | 0 | 807.65 | 4845.9 | ITC1 | B
IT | ITC11 |  | IT01000000000042 | BARDONECCHIA | 45.07 | 6.7183 | 9000 | 10539 | NO | 65.8688 | 0 | 0 | 0 | 382.0388 | 2292.2325 | ITC1 | C
IT | ITC13 |  | IT01000000000041 | BIELLA_NORD | 45.5418 | 8.0414 | 67000 | 34850 | NO | 217.8125 | 0 | 0 | 0 | 1263.3125 | 7579.875 | ITC1 | A
IT | ITC18 |  | IT01000000000040 | VALENZA | 45.0159 | 8.6568 | 30000 | 18450 | NO | 115.3125 | 0 | 0 | 0 | 668.8125 | 4012.875 | ITC1 | B
IT | ITC13 |  | IT01000000000039 | LAGO DI VIVERONE | 45.4182 | 7.9801 | 5000 | 5200 | NO | 32.5 | 0 | 0 | 0 | 188.5 | 1131 | ITC1 | B
IT | ITC18 |  | IT01000000000038 | CASALE_MONFERRATO | 45.1385 | 8.4838 | 58000 | 43152 | NO | 269.7 | 0 | 0 | 0 | 1564.26 | 9385.56 | ITC1 | C
IT | ITC12 |  | IT01000000000037 | SALUGGIA | 45.2279 | 8.0249 | 5000 | 2790 | NO | 17.4375 | 0 | 0 | 0 | 101.1375 | 606.825 | ITC1 | B
IT | ITC11 |  | IT01000000000036 | CRESCENTINO | 45.1895 | 8.1157 | 6000 | 6000 | NO | 37.5 | 0 | 0 | 0 | 217.5 | 1305 | ITC1 | B
IT | ITC11 |  | IT01000000000046 | CHIERI | 44.9824 | 7.8124 | 75000 | 54134 | NO | 338.3375 | 0 | 0 | 0 | 1962.3575 | 11774.145 | ITC1 | C
IT | ITC14 |  | IT01000000000011 | VERBANIA_SPV | 45.9351 | 8.5594 | 55000 | 47265 | NO | 295.4062 | 0 | 0 | 0 | 1713.3562 | 10280.1375 | ITC1 | A
IT | ITC16 |  | IT01Q13000000005 | NARZOLE | 44.6047 | 7.8764 | 20000 | 11064 | NO | 69.15 | 0 | 0 | 0 | 401.07 | 2406.42 | ITC1 | B
IT | ITC12 |  | IT01Q90000001431 | CARESANABLOT | 45.3552 | 8.4027 | 5000 | 2957 | NO | 18.4812 | 0 | 0 | 0 | 107.1912 | 643.1475 | ITC1 | B
IT | ITC11 |  | IT01Q13000000000 | VOLVERA_CASTAGNOLE | 44.9726 | 7.5244 | 5000 | 5322 | NO | 33.2625 | 0 | 0 | 0 | 192.9225 | 1157.535 | ITC1 | B
IT | ITC12 |  | IT01Q11000000008 | LIVORNO_FERRARIS | 45.2723 | 8.0922 | 5000 | 4825 | NO | 30.1562 | 0 | 0 | 0 | 174.9062 | 1049.4375 | ITC1 | C
IT | ITC18 |  | IT01Q11000000007 | FRUGAROLO | 44.8433 | 8.6727 | 12500 | 5640 | NO | 35.25 | 0 | 0 | 0 | 204.45 | 1226.7 | ITC1 | B
IT | ITC16 |  | IT01Q11000000006 | FRABOSA_SOTTANA_PRATO_NEVOSO | 44.26 | 7.7809 | 8200 | 8140 | NO | 50.875 | 0 | 0 | 0 | 295.075 | 1770.45 | ITC1 | B
IT | ITC16 |  | IT01Q11000000005 | FOSSANO_LOC_STURA | 44.5588 | 7.7572 | 30000 | 19200 | NO | 120 | 0 | 0 | 0 | 696 | 4176 | ITC1 | C
IT | ITC18 |  | IT01Q11000000001 | BORGHETTO_BORBERA | 44.7249 | 8.925 | 5100 | 2602 | NO | 16.2625 | 0 | 0 | 0 | 94.3225 | 565.935 | ITC1 | C
IT | ITC11 |  | IT01Q13000000004 | CAVOUR_FRAZ_CASTELLAZZO | 44.8273 | 7.4044 | 20000 | 19277 | NO | 120.4813 | 0 | 0 | 0 | 698.7912 | 4192.7475 | ITC1 | C
IT | ITC14 |  | IT01000000000008 | VILLADOSSOLA | 46.0528 | 8.2646 | 8000 | 5311 | NO | 33.1938 | 0 | 0 | 0 | 192.5238 | 1155.1425 | ITC1 | B
IT | ITC11 |  | IT01000000000007 | VOGOGNA_NORD | 46.0295 | 8.2795 | 8000 | 5053 | NO | 31.5813 | 0 | 0 | 0 | 183.1713 | 1099.0275 | ITC1 | A
IT | ITC11 |  | IT01000000000006 | VOGOGNA_SUD | 46.0005 | 8.2986 | 8000 | 3981 | NO | 24.8812 | 0 | 0 | 0 | 144.3112 | 865.8675 | ITC1 | B
IT | ITC14 |  | IT01000000000005 | GRAVELLONA | 45.9367 | 8.4323 | 18000 | 20668 | NO | 129.175 | 0 | 0 | 0 | 749.215 | 4495.29 | ITC1 | A
IT | ITC14 |  | IT01000000000004 | MERGOZZO | 45.963 | 8.4353 | 9225 | 7711 | NO | 48.1938 | 0 | 0 | 0 | 279.5238 | 1677.1425 | ITC1 | B
IT | ITC14 |  | IT01000000000003 | LESA | 45.8169 | 8.5546 | 28000 | 15625 | NO | 97.6562 | 0 | 0 | 0 | 566.4062 | 3398.4375 | ITC1 | A
IT | ITC15 |  | IT01000000000002 | LAGNA | 45.7855 | 8.3896 | 14500 | 5514 | NO | 34.4625 | 0 | 0 | 0 | 199.8825 | 1199.295 | ITC1 | B
IT | ITC14 |  | IT01000000000001 | OMEGNA_ACQUE_CUSIO | 45.9009 | 8.4209 | 29000 | 27059 | NO | 169.1188 | 0 | 0 | 0 | 980.8888 | 5885.3325 | ITC1 | A
IT | ITC14 |  | IT01Q90000002533 | RE_MEIS | 46.1336 | 8.5583 | 9000 | 4266 | NO | 26.6625 | 0 | 0 | 0 | 154.6425 | 927.855 | ITC1 | C
IT | ITC16 |  | IT01000000000137 | SANTO_STEFANO_BELBO | 44.7116 | 8.2549 | 120000 | 88837 | NO | 555.2313 | 0 | 0 | 0 | 3220.3413 | 19322.0475 | ITC1 | C
IT | ITC18 |  | IT01000000000157 | CASSANO_SPINOLA | 44.7683 | 8.8522 | 100000 | 63315 | NO | 395.7188 | 0 | 0 | 0 | 2295.1687 | 13771.0125 | ITC1 | B
IT | ITC18 |  | IT01000000000163 | CASTELNUOVO_SCRIVIA | 44.9903 | 8.8783 | 12697 | 7308 | NO | 45.675 | 0 | 0 | 0 | 264.915 | 1589.49 | ITC1 | B
IT | ITC18 |  | IT01000000000162 | OVADA | 44.6526 | 8.65 | 18000 | 16020 | NO | 100.125 | 0 | 0 | 0 | 580.725 | 3484.35 | ITC1 | A
IT | ITC18 |  | IT01000000000161 | NOVI_LIGURE | 44.7864 | 8.7575 | 90000 | 78000 | YES | 487.5 | 1560 | 1170 | 2340 | 2827.5 | 16965 | ITC1 | A
IT | ITC11 |  | IT01000000000092 | OSASCO_SAN_SECONDO_PRAROSTINO | 44.85 | 7.355 | 5441 | 4742 | NO | 29.6375 | 0 | 0 | 0 | 171.8975 | 1031.385 | ITC1 | C
IT | ITC16 |  | IT01000000000112 | MONDOVI | 44.406 | 7.8481 | 28000 | 24600 | NO | 153.75 | 0 | 0 | 0 | 891.75 | 5350.5 | ITC1 | C
IT | ITC16 |  | IT01000000000107 | CHERASCO | 44.656 | 7.867 | 10500 | 10352 | NO | 64.7 | 0 | 0 | 0 | 375.26 | 2251.56 | ITC1 | B
IT | ITC16 |  | IT01000000000105 | CEVA | 44.397 | 8.0157 | 10000 | 6390 | NO | 39.9375 | 0 | 0 | 0 | 231.6375 | 1389.825 | ITC1 | C
IT | ITC18 |  | IT01000000000156 | TORTONA | 44.9179 | 8.8719 | 83000 | 41411 | YES | 258.8188 | 828.22 | 621.165 | 1242.33 | 1501.1488 | 9006.8925 | ITC1 | C
IT | ITC17 |  | IT01000000000155 | NIZZA_MONFERRATO | 44.7769 | 8.3743 | 30000 | 12125 | NO | 75.7812 | 0 | 0 | 0 | 439.5312 | 2637.1875 | ITC1 | B
IT | ITC17 |  | IT01000000000154 | CANELLI | 44.7215 | 8.3014 | 21000 | 16596 | NO | 103.725 | 0 | 0 | 0 | 601.605 | 3609.63 | ITC1 | A
IT | ITC17 |  | IT01000000000153 | INCISA_SCAPACCINO | 44.8105 | 8.3812 | 6000 | 4000 | NO | 25 | 0 | 0 | 0 | 145 | 870 | ITC1 | A
IT | ITC17 |  | IT01000000000152 | CALAMANDRANA | 44.7439 | 8.3319 | 6400 | 5400 | NO | 33.75 | 0 | 0 | 0 | 195.75 | 1174.5 | ITC1 | B
IT | ITC17 |  | IT01000000000151 | SAN_DAMIANO | 44.8423 | 8.077 | 8000 | 6150 | NO | 38.4375 | 0 | 0 | 0 | 222.9375 | 1337.625 | ITC1 | C
IT | ITC17 |  | IT01000000000149 | VILLANOVA_D_ASTI | 44.9363 | 7.9339 | 7500 | 5269 | NO | 32.9312 | 0 | 0 | 0 | 191.0012 | 1146.0075 | ITC1 | B
IT | ITC18 |  | IT01000000000159 | ACQUI_TERME_FONTANELLE | 44.6752 | 8.4863 | 45000 | 26565 | NO | 166.0312 | 0 | 0 | 0 | 962.9813 | 5777.8875 | ITC1 | B
IT | ITC11 |  | IT01000000000078 | COLLEGNO | 45.0925 | 7.6099 | 267000 | 168246 | YES | 1051.5375 | 3364.92 | 2523.69 | 5047.38 | 6098.9175 | 36593.505 | ITC1 | A
IT | ITC11 |  | IT01000000000091 | PINEROLO_PORTE | 44.884 | 7.3607 | 75000 | 89175 | YES | 557.3438 | 1783.5 | 1337.625 | 2675.25 | 3232.5938 | 19395.5625 | ITC1 | B
IT | ITC11 |  | IT01000000000084 | CESANA_TORINESE_MOLLIERES | 44.9647 | 6.7952 | 6000 | 3892 | NO | 24.325 | 0 | 0 | 0 | 141.085 | 846.51 | ITC1 | C
IT | ITC11 |  | IT01000000000081 | ACSEL_ROSTA | 45.0892 | 7.4812 | 99000 | 84729 | YES | 529.5562 | 1694.58 | 1270.935 | 2541.87 | 3071.4262 | 18428.5575 | ITC1 | A
IT | ITC16 |  | IT01000000000124 | ENTRACQUE | 44.2413 | 7.3925 | 5000 | 4800 | NO | 30 | 0 | 0 | 0 | 174 | 1044 | ITC1 | B
IT | ITC11 |  | IT01000000000079 | AIDA_PIANEZZA | 45.0894 | 7.5622 | 88330 | 53176 | NO | 332.35 | 0 | 0 | 0 | 1927.63 | 11565.78 | ITC1 | B
IT | ITH31 |  | IT05000000000001 | BOVOLONE_VIA_VALLE_DEL_MENAGO | 45.248 | 11.125 | 18500 | 15187 | NO | 94.9188 | 0 | 0 | 0 | 550.5287 | 3303.1725 | ITH3 | B
IT | ITH31 |  | IT05000000000004 | PESCANTINA_TREMOLE_ | 45.474 | 10.877 | 12000 | 10741 | NO | 67.1313 | 0 | 0 | 0 | 389.3613 | 2336.1675 | ITH3 | B
IT | ITH31 |  | IT05000000000005 | BUSSOLENGO_ALBERE | 45.477 | 10.871 | 18000 | 19177 | NO | 119.8563 | 0 | 0 | 0 | 695.1662 | 4170.9975 | ITH3 | B
IT | ITH31 |  | IT05000000000006 | SAN_MARTINO_BUON_ALBERGO_CA_DELL_AGLIO | 45.411 | 11.108 | 20000 | 17802 | NO | 111.2625 | 0 | 0 | 0 | 645.3225 | 3871.935 | ITH3 | B
IT | ITH31 |  | IT05000000000007 | CALDIERO_BATTAIOLE | 45.393 | 11.158 | 30000 | 26702 | NO | 166.8875 | 0 | 0 | 0 | 967.9475 | 5807.685 | ITH3 | C
IT | ITH31 |  | IT05000000000008 | CAPRINO_VERONESE_MONTESEI_PESINA | 45.587 | 10.764 | 10000 | 9135 | NO | 57.0938 | 0 | 0 | 0 | 331.1437 | 1986.8625 | ITH3 | B
IT | ITH31 |  | IT05000000000009 | CASTEL_D_AZZANO_SAN_MARTINO | 45.345 | 10.949 | 20000 | 15753 | NO | 98.4563 | 0 | 0 | 0 | 571.0463 | 3426.2775 | ITH3 | B
IT | ITH33 |  | IT05Q90000003230 | LA_VALLE_AGORDINA_LE_CAMPE | 46.259 | 12.044 | 7500 | 4061 | NO | 25.3812 | 0 | 0 | 0 | 147.2112 | 883.2675 | ITH3 | C
IT | ITH33 |  | IT05Q90000003237 | SAN_VITO_DI_CADORE_LOC_CIAMPES | 46.453 | 12.205 | 7850 | 4410 | NO | 27.5625 | 0 | 0 | 0 | 159.8625 | 959.175 | ITH3 | B
IT | ITC11 |  | IT01000000000097 | CUMIANA_CHISOLA | 44.9782 | 7.389 | 5000 | 5960 | NO | 37.25 | 0 | 0 | 0 | 216.05 | 1296.3 | ITC1 | B
IT | ITC11 |  | IT01000000000076 | CARIGNANO | 44.9122 | 7.682 | 9450 | 9255 | NO | 57.8438 | 0 | 0 | 0 | 335.4937 | 2012.9625 | ITC1 | B
IT | ITC11 |  | IT01000000000075 | CARMAGNOLA_CEIS | 44.8669 | 7.7071 | 38000 | 27778 | NO | 173.6125 | 0 | 0 | 0 | 1006.9525 | 6041.715 | ITC1 | B
IT | ITC11 |  | IT01000000000072 | LANZO_TORINESE | 45.2672 | 7.4996 | 8000 | 6237 | NO | 38.9813 | 0 | 0 | 0 | 226.0913 | 1356.5475 | ITC1 | A
IT | ITC11 |  | IT01000000000071 | CUORGNE_VALPERGA | 45.3733 | 7.6859 | 17600 | 17472 | NO | 109.2 | 0 | 0 | 0 | 633.36 | 3800.16 | ITC1 | C
IT | ITC11 |  | IT01000000000068 | RIVARA | 45.32 | 7.6542 | 18000 | 7942 | NO | 49.6375 | 0 | 0 | 0 | 287.8975 | 1727.385 | ITC1 | B
IT | ITC11 |  | IT01000000000067 | BOSCONERO | 45.2572 | 7.7709 | 12000 | 5798 | NO | 36.2375 | 0 | 0 | 0 | 210.1775 | 1261.065 | ITC1 | B
IT | ITC11 |  | IT01000000000080 | GIAVENO | 45.0253 | 7.3814 | 28000 | 22350 | NO | 139.6875 | 0 | 0 | 0 | 810.1875 | 4861.125 | ITC1 | C
IT | ITC11 |  | IT01000000000064 | IVREA_EST | 45.4467 | 7.9125 | 26000 | 24899 | NO | 155.6188 | 0 | 0 | 0 | 902.5888 | 5415.5325 | ITC1 | A
IT | ITC16 |  | IT01000000000121 | BUSCA | 44.5167 | 7.4824 | 9000 | 7156 | NO | 44.725 | 0 | 0 | 0 | 259.405 | 1556.43 | ITC1 | B
IT | ITC16 |  | IT01000000000120 | CENTALLO | 44.5125 | 7.5904 | 7017 | 4966 | NO | 31.0375 | 0 | 0 | 0 | 180.0175 | 1080.105 | ITC1 | C
IT | ITC16 |  | IT01000000000119 | CUNEO | 44.4021 | 7.5559 | 185000 | 132620 | YES | 828.875 | 2652.4 | 1989.3 | 3978.6 | 4807.475 | 28844.85 | ITC1 | A
IT | ITC16 |  | IT01000000000117 | VERZUOLO | 44.6056 | 7.4917 | 6500 | 5210 | NO | 32.5625 | 0 | 0 | 0 | 188.8625 | 1133.175 | ITC1 | B
IT | ITC16 |  | IT01000000000116 | SAVIGLIANO | 44.6649 | 7.6592 | 22700 | 17250 | NO | 107.8125 | 0 | 0 | 0 | 625.3125 | 3751.875 | ITC1 | B
IT | ITC16 |  | IT01000000000115 | SALUZZO | 44.6554 | 7.4742 | 38000 | 33431 | NO | 208.9438 | 0 | 0 | 0 | 1211.8737 | 7271.2425 | ITC1 | B
IT | ITC11 |  | IT01000000000102 | VILLAFRANCA_PIEMONTE | 44.7829 | 7.511 | 5000 | 4414 | NO | 27.5875 | 0 | 0 | 0 | 160.0075 | 960.045 | ITC1 | A
IT | ITC11 |  | IT01000000000099 | PRAGELATO | 45.0191 | 6.9478 | 6000 | 2933 | NO | 18.3313 | 0 | 0 | 0 | 106.3213 | 637.9275 | ITC1 | A
IT | ITC11 |  | IT01000000000098 | VIGONE | 44.836 | 7.5088 | 5400 | 5207 | NO | 32.5438 | 0 | 0 | 0 | 188.7538 | 1132.5225 | ITC1 | B
IT | ITC20 |  | IT02Q13000000000 | BRISSOGNE | 45.7348 | 7.3795 | 150000 | 62148 | YES | 388.425 | 1242.96 | 932.22 | 1864.44 | 2252.865 | 13517.19 | ITC2 | A
IT | ITC20 |  | IT02Q13000000002 | ARNAD | 45.6392 | 7.7176 | 13000 | 1589 | NO | 9.9313 | 0 | 0 | 0 | 57.6012 | 345.6075 | ITC2 | A
IT | ITC20 |  | IT02Q13000000003 | GLEREYAZ | 45.7459 | 7.6289 | 9000 | 6736 | NO | 42.1 | 0 | 0 | 0 | 244.18 | 1465.08 | ITC2 | B
IT | ITC20 |  | IT02Q13000000005 | ANTEY_SAINT_ANDRE | 45.7774 | 7.5933 | 13200 | 4351 | NO | 27.1937 | 0 | 0 | 0 | 157.7237 | 946.3425 | ITC2 | C
IT | ITC20 |  | IT02Q13000000007 | LILLIANES | 45.6258 | 7.8324 | 10000 | 6762 | NO | 42.2625 | 0 | 0 | 0 | 245.1225 | 1470.735 | ITC2 | C
IT | ITC20 |  | IT02Q13000000008 | GRESSONEY_TRINO | 45.7386 | 7.8533 | 20000 | 1997 | NO | 12.4813 | 0 | 0 | 0 | 72.3912 | 434.3475 | ITC2 | C
IT | ITC20 |  | IT02Q13000000013 | CHAMPORCHER | 45.6215 | 7.6322 | 5000 | 388 | NO | 2.425 | 0 | 0 | 0 | 14.065 | 84.39 | ITC2 | C
IT | ITC20 |  | IT02Q15000000015 | COGNE | 45.6125 | 7.3477 | 10000 | 3000 | NO | 18.75 | 0 | 0 | 0 | 108.75 | 652.5 | ITC2 | A
IT | ITH34 |  | IT05000000000142 | CASTELFRANCO_BORGO_PADOVA | 45.654 | 11.94 | 40000 | 33573 | NO | 209.8312 | 0 | 0 | 0 | 1217.0212 | 7302.1275 | ITH3 | B
IT | ITH34 |  | IT05000000000143 | CASTELFRANCO_SALVATRONDA | 45.664 | 11.979 | 73300 | 61522 | NO | 384.5125 | 0 | 0 | 0 | 2230.1725 | 13381.035 | ITH3 | C
IT | ITH34 |  | IT05000000000146 | MARENO_DI_PIAVE_PIAZZA_VITTORIO_EMANUELE_III | 45.848 | 12.357 | 7000 | 4400 | NO | 27.5 | 0 | 0 | 0 | 159.5 | 957 | ITH3 | B
IT | ITC43 |  | IT03160129000797 | DP09708301_VALMADRERA | 45.8523 | 9.3683 | 99303 | 65660 | YES | 410.375 | 1313.2 | 984.9 | 1969.8 | 2380.175 | 14281.05 | ITC4 | B
IT | ITC43 |  | IT03160129000800 | DP09708701_VERDERIO_INFERIORE | 45.6586 | 9.4239 | 20000 | 19946 | NO | 124.6625 | 0 | 0 | 0 | 723.0425 | 4338.255 | ITC4 | B
IT | ITC49 |  | IT03160129000803 | DP09800901_CASALMAIOCCO | 45.3483 | 9.3695 | 5300 | 2632 | NO | 16.45 | 0 | 0 | 0 | 95.41 | 572.46 | ITC4 | A
IT | ITC49 |  | IT03160129000804 | DP09801001_CASALPUSTERLENGO | 45.1665 | 9.6565 | 30000 | 19031 | NO | 118.9438 | 0 | 0 | 0 | 689.8737 | 4139.2425 | ITC4 | B
IT | ITC49 |  | IT03160129000807 | DP09801401_CASTIGLIONE_D_ADDA | 45.2239 | 9.6898 | 5000 | 5113 | NO | 31.9563 | 0 | 0 | 0 | 185.3462 | 1112.0775 | ITC4 | A
IT | ITC49 |  | IT03160129000808 | DP09801901_CODOGNO | 45.1544 | 9.7116 | 22000 | 19613 | NO | 122.5813 | 0 | 0 | 0 | 710.9713 | 4265.8275 | ITC4 | A
IT | ITH31 |  | IT05000000000040 | RONCO_ALL_ADIGE_QUADRELLI | 45.327 | 11.247 | 7000 | 5787 | NO | 36.1688 | 0 | 0 | 0 | 209.7788 | 1258.6725 | ITH3 | B
IT | ITH31 |  | IT05000000000041 | ZEVIO_TRE_CORONE | 45.366 | 11.141 | 14000 | 8832 | NO | 55.2 | 0 | 0 | 0 | 320.16 | 1920.96 | ITH3 | B
IT | ITH31 |  | IT05000000000042 | SANT_AMBROGIO_DI_VALPOLICELLA_PONTON | 45.516 | 10.805 | 30000 | 17581 | NO | 109.8813 | 0 | 0 | 0 | 637.3112 | 3823.8675 | ITH3 | B
IT | ITH32 |  | IT05000000000043 | ARZIGNANO_VIA_ALTURA | 45.502 | 11.377 | 2360000 | 991650 | YES | 6197.8125 | 19833 | 14874.75 | 29749.5 | 35947.3125 | 215683.875 | ITH3 | A
IT | ITH32 |  | IT05000000000044 | BARBARANO_VICENTINO_PONTE | 45.378 | 11.575 | 7500 | 4247 | NO | 26.5438 | 0 | 0 | 0 | 153.9538 | 923.7225 | ITH3 | A
IT | ITH32 |  | IT05000000000045 | BASSANO_DEL_GRAPPA_VIA_SAN_LAZZARO | 45.739 | 11.702 | 96000 | 68044 | YES | 425.275 | 1360.88 | 1020.66 | 2041.32 | 2466.595 | 14799.57 | ITH3 | B
IT | ITH32 |  | IT05000000000054 | GRISIGNANO_DI_ZOCCO_VIA_KENNEDY | 45.461 | 11.71 | 43000 | 29254 | NO | 182.8375 | 0 | 0 | 0 | 1060.4575 | 6362.745 | ITH3 | B
IT | ITH32 |  | IT05000000000055 | ISOLA_VICENTINA_VIA_VICENZA | 45.601 | 11.481 | 40288 | 38102 | NO | 238.1375 | 0 | 0 | 0 | 1381.1975 | 8287.185 | ITH3 | C
IT | ITH32 |  | IT05000000000056 | LONIGO_VIA_LORE | 45.372 | 11.376 | 50000 | 29413 | NO | 183.8312 | 0 | 0 | 0 | 1066.2212 | 6397.3275 | ITH3 | B
IT | ITH32 |  | IT05000000000059 | MONTEBELLO_VICENTINO_VIA_FRACANZANA | 45.438 | 11.377 | 472000 | 263460 | YES | 1646.625 | 5269.2 | 3951.9 | 7903.8 | 9550.425 | 57302.55 | ITH3 | A
IT | ITH32 |  | IT05000000000060 | MONTECCHIO_MAGGIORE_VIA_CALLESELLA | 45.485 | 11.434 | 70000 | 29413 | NO | 183.8312 | 0 | 0 | 0 | 1066.2212 | 6397.3275 | ITH3 | A
IT | ITH32 |  | IT05000000000061 | CASTEGNERO_VIA_FRASSENA | 45.432 | 11.607 | 5500 | 4878 | NO | 30.4875 | 0 | 0 | 0 | 176.8275 | 1060.965 | ITH3 | B
IT | ITH32 |  | IT05000000000063 | NOVENTA_VICENTINA_VIA_DE_GASPERI | 45.281 | 11.537 | 9800 | 7876 | NO | 49.225 | 0 | 0 | 0 | 285.505 | 1713.03 | ITH3 | B
IT | ITH32 |  | IT05000000000065 | SANDRIGO_VIA_ALBARETTO | 45.654 | 11.607 | 9000 | 7974 | NO | 49.8375 | 0 | 0 | 0 | 289.0575 | 1734.345 | ITH3 | B
IT | ITH32 |  | IT05000000000066 | SCHIO_VIA_CA_CAPRETTA | 45.713 | 11.403 | 60000 | 55705 | NO | 348.1562 | 0 | 0 | 0 | 2019.3062 | 12115.8375 | ITH3 | A
IT | ITH32 |  | IT05000000000071 | TEZZE_SUL_BRENTA_VIA_BRENTA | 45.671 | 11.692 | 100000 | 48977 | NO | 306.1062 | 0 | 0 | 0 | 1775.4162 | 10652.4975 | ITH3 | A
IT | ITH32 |  | IT05000000000077 | ASIAGO_LOCALITA_MOSELE | 45.857 | 11.483 | 35000 | 13870 | NO | 86.6875 | 0 | 0 | 0 | 502.7875 | 3016.725 | ITH3 | C
IT | ITH32 |  | IT05000000000078 | THIENE_SANTO | 45.665 | 11.488 | 127000 | 113885 | YES | 711.7812 | 2277.7 | 1708.275 | 3416.55 | 4128.3313 | 24769.9875 | ITH3 | B
IT | ITH32 |  | IT05000000000079 | TRISSINO_PRANOVI | 45.542 | 11.383 | 127500 | 63029 | YES | 393.9313 | 1260.58 | 945.435 | 1890.87 | 2284.8012 | 13708.8075 | ITH3 | A
IT | ITH32 |  | IT05000000000083 | CREAZZO_VIA_BRESCIA | 45.526 | 11.48 | 12500 | 10987 | NO | 68.6688 | 0 | 0 | 0 | 398.2788 | 2389.6725 | ITH3 | B
IT | ITH32 |  | IT05000000000084 | CALDOGNO_VIA_M_T_DI_CALCUTTA | 45.587 | 11.524 | 13500 | 10074 | NO | 62.9625 | 0 | 0 | 0 | 365.1825 | 2191.095 | ITH3 | B
IT | ITH32 |  | IT05000000000085 | DUEVILLE_VIVARO | 45.603 | 11.549 | 22000 | 20416 | NO | 127.6 | 0 | 0 | 0 | 740.08 | 4440.48 | ITH3 | C
IT | ITH32 |  | IT05000000000086 | VICENZA_SANT_AGOSTINO | 45.522 | 11.515 | 100000 | 87897 | NO | 549.3563 | 0 | 0 | 0 | 3186.2662 | 19117.5975 | ITH3 | A
IT | ITH32 |  | IT05000000000087 | VICENZA_CASALE | 45.52 | 11.578 | 92000 | 83063 | YES | 519.1438 | 1661.26 | 1245.945 | 2491.89 | 3011.0338 | 18066.2025 | ITH3 | C
IT | ITH33 |  | IT05000000000099 | AURONZO_DI_CADORE_TARLISSE | 46.535 | 12.467 | 17500 | 7772 | NO | 48.575 | 0 | 0 | 0 | 281.735 | 1690.41 | ITH3 | C
IT | ITH33 |  | IT05000000000100 | BELLUNO_MARISIGA | 46.125 | 12.193 | 32000 | 32046 | NO | 200.2875 | 0 | 0 | 0 | 1161.6675 | 6970.005 | ITH3 | C
IT | ITH33 |  | IT05000000000105 | CORTINA_PIAN_DE_RASPINIS | 46.506 | 12.145 | 18500 | 18496 | NO | 115.6 | 0 | 0 | 0 | 670.48 | 4022.88 | ITH3 | A
IT | ITH33 |  | IT05000000000106 | FELTRE_STAZIONE_FERROVIARIA | 46.012 | 11.913 | 102600 | 35522 | NO | 222.0125 | 0 | 0 | 0 | 1287.6725 | 7726.035 | ITH3 | A
IT | ITH33 |  | IT05000000000122 | LONGARONE_RIVALTA_CAPOLUOGO | 46.259 | 12.307 | 6000 | 2734 | NO | 17.0875 | 0 | 0 | 0 | 99.1075 | 594.645 | ITH3 | B
IT | ITH33 |  | IT05000000000125 | PIEVE_D_ALPAGO_Z_IND_PALUDI | 46.143 | 12.325 | 8000 | 7526 | NO | 47.0375 | 0 | 0 | 0 | 272.8175 | 1636.905 | ITH3 | A
IT | ITH33 |  | IT05000000000127 | CALALZO_DI_CADORE_COL_DEI_CAI | 46.444 | 12.395 | 6000 | 4115 | NO | 25.7188 | 0 | 0 | 0 | 149.1687 | 895.0125 | ITH3 | B
IT | ITH33 |  | IT05000000000128 | DOMEGGE_DI_CADORE_PIANI_DI_VALLESELLA | 46.453 | 12.41 | 6000 | 3064 | NO | 19.15 | 0 | 0 | 0 | 111.07 | 666.42 | ITH3 | B
IT | ITH33 |  | IT05000000000129 | PONTE_NELLE_ALPI_LA_NA_ | 46.176 | 12.278 | 5000 | 4935 | NO | 30.8438 | 0 | 0 | 0 | 178.8937 | 1073.3625 | ITH3 | B
IT | ITH33 |  | IT05000000000131 | SANTA_GIUSTINA_FORMEGAN | 46.066 | 12.027 | 5000 | 4163 | NO | 26.0188 | 0 | 0 | 0 | 150.9087 | 905.4525 | ITH3 | B
IT | ITH33 |  | IT05000000000133 | SEDICO_OSELETE | 46.085 | 12.085 | 6000 | 4962 | NO | 31.0125 | 0 | 0 | 0 | 179.8725 | 1079.235 | ITH3 | C
IT | ITH34 |  | IT05000000000135 | CARBONERA_VIA_BIANCHINI | 45.674 | 12.292 | 43200 | 48756 | NO | 304.725 | 0 | 0 | 0 | 1767.405 | 10604.43 | ITH3 | B
IT | ITH34 |  | IT05000000000136 | CASIER_DOSSON,_VIA_BIGONZO | 45.608 | 12.264 | 12000 | 8150 | NO | 50.9375 | 0 | 0 | 0 | 295.4375 | 1772.625 | ITH3 | B
IT | ITH32 |  | IT05000000000141 | MUSSOLENTE_CAMPO_AVIAZIONE | 45.752 | 11.827 | 22000 | 11204 | NO | 70.025 | 0 | 0 | 0 | 406.145 | 2436.87 | ITH3 | C
IT | ITC20 |  | IT02Q90000000592 | USSIN | 45.8504 | 7.6056 | 40000 | 14188 | NO | 88.675 | 0 | 0 | 0 | 514.315 | 3085.89 | ITC2 | C
IT | ITC20 |  | IT02Q90000000593 | AYAS_CORBET | 45.7967 | 7.6964 | 20000 | 7000 | NO | 43.75 | 0 | 0 | 0 | 253.75 | 1522.5 | ITC2 | C
IT | ITC20 |  | IT02Q90000000604 | SAINT_VINCENT | 45.7438 | 7.6445 | 8000 | 4888 | NO | 30.55 | 0 | 0 | 0 | 177.19 | 1063.14 | ITC2 | B
IT | ITH34 |  | IT05000000000148 | CORDIGNANO_VIA_PALU_ | 45.935 | 12.458 | 30000 | 28068 | NO | 175.425 | 0 | 0 | 0 | 1017.465 | 6104.79 | ITH3 | B
IT | ITH34 |  | IT05000000000150 | CROCETTA_DEL_MONTELLO_VIA_BARACCA | 45.826 | 12.058 | 5500 | 5443 | NO | 34.0188 | 0 | 0 | 0 | 197.3088 | 1183.8525 | ITH3 | A
IT | ITH34 |  | IT05000000000151 | REVINE_LAGO_LAGO | 45.977 | 12.199 | 5000 | 4690 | NO | 29.3125 | 0 | 0 | 0 | 170.0125 | 1020.075 | ITH3 | C
IT | ITH34 |  | IT05000000000152 | GIAVERA_DEL_MONTELLO_CUSIGNANA,_VIA_TONIOLO | 45.772 | 12.202 | 18000 | 12347 | NO | 77.1688 | 0 | 0 | 0 | 447.5788 | 2685.4725 | ITH3 | B
IT | ITH34 |  | IT05000000000153 | MONTEBELLUNA_SAN_GAETANO | 45.743 | 12.046 | 32000 | 29944 | NO | 187.15 | 0 | 0 | 0 | 1085.47 | 6512.82 | ITH3 | C
IT | ITH34 |  | IT05000000000155 | ODERZO_FRATTA_SX_MOTICANO | 45.788 | 12.511 | 14000 | 7068 | NO | 44.175 | 0 | 0 | 0 | 256.215 | 1537.29 | ITH3 | B
IT | ITH34 |  | IT05000000000156 | ODERZO_SPINE_ | 45.775 | 12.497 | 18000 | 13117 | NO | 81.9813 | 0 | 0 | 0 | 475.4912 | 2852.9475 | ITH3 | B
IT | ITH35 |  | IT05000000000191 | MEOLO_VIA_MARTEGGIA | 45.609 | 12.46 | 9000 | 6508 | NO | 40.675 | 0 | 0 | 0 | 235.915 | 1415.49 | ITH3 | B
IT | ITH35 |  | IT05000000000193 | MUSILE_VIA_ROVIGO,_13 | 45.628 | 12.543 | 9640 | 8334 | NO | 52.0875 | 0 | 0 | 0 | 302.1075 | 1812.645 | ITH3 | B
IT | ITH35 |  | IT05000000000201 | PORTOGRUARO_VIA_VENEZIA | 45.77 | 12.827 | 10000 | 9800 | NO | 61.25 | 0 | 0 | 0 | 355.25 | 2131.5 | ITH3 | B
IT | ITH35 |  | IT05000000000205 | QUARTO_D_ALTINO_VIA_MARCONI | 45.575 | 12.38 | 50000 | 43878 | NO | 274.2375 | 0 | 0 | 0 | 1590.5775 | 9543.465 | ITH3 | B
IT | ITH35 |  | IT05000000000207 | SAN_DONA_DI_PIAVE_VIA_TRONCO | 45.622 | 12.602 | 45000 | 38852 | NO | 242.825 | 0 | 0 | 0 | 1408.385 | 8450.31 | ITH3 | B
IT | ITH36 |  | IT05000000000228 | TOMBOLO_VIA_CAMPOLONGO_ONARA | 45.617 | 11.825 | 12000 | 8706 | NO | 54.4125 | 0 | 0 | 0 | 315.5925 | 1893.555 | ITH3 | C
IT | ITH36 |  | IT05000000000229 | CITTADELLA_VIA_DELLE_SANSUGHE | 45.639 | 11.795 | 60000 | 43540 | NO | 272.125 | 0 | 0 | 0 | 1578.325 | 9469.95 | ITH3 | B
IT | ITH36 |  | IT05000000000230 | CODEVIGO_VIA_ALTIPIANO | 45.247 | 12.107 | 65000 | 46401 | NO | 290.0063 | 0 | 0 | 0 | 1682.0362 | 10092.2175 | ITH3 | C
IT | ITH36 |  | IT05000000000231 | CONSELVE_VIA_DELL_INDUSTRIA_ZI | 45.203 | 11.901 | 46880 | 28686 | NO | 179.2875 | 0 | 0 | 0 | 1039.8675 | 6239.205 | ITH3 | A
IT | ITC20 |  | IT02Q90000000607 | SAINT_MARCEL | 45.7389 | 7.4513 | 19000 | 9000 | NO | 56.25 | 0 | 0 | 0 | 326.25 | 1957.5 | ITC2 | B
IT | ITC20 |  | IT02Q190000001 | EQUILIVAZ | 45.7196 | 7.104 | 60000 | 3500 | NOT KNOWN | 21.875 | 0 | 0 | 0 | 126.875 | 761.25 | ITC2 | C
IT | ITH35 |  | IT05000000000208 | SAN_MICHELE_AL_TAGLIAMENTO_VIA_ALDO_MORO | 45.756 | 12.987 | 8000 | 5634 | NO | 35.2125 | 0 | 0 | 0 | 204.2325 | 1225.395 | ITH3 | B
IT | ITH35 |  | IT05000000000209 | SAN_MICHELE_AL_TAGLIAMENTO_VIA_PARENZO | 45.642 | 13.075 | 150000 | 109150 | YES | 682.1875 | 2183 | 1637.25 | 3274.5 | 3956.6875 | 23740.125 | ITH3 | B
IT | ITH35 |  | IT05000000000211 | VENEZIA_LIDO | 45.364 | 12.335 | 30000 | 23725 | NO | 148.2812 | 0 | 0 | 0 | 860.0312 | 5160.1875 | ITH3 | A
IT | ITH35 |  | IT05000000000212 | VENEZIA_CAMPALTO | 45.485 | 12.307 | 130000 | 115482 | YES | 721.7625 | 2309.64 | 1732.23 | 3464.46 | 4186.2225 | 25117.335 | ITH3 | A
IT | ITH35 |  | IT05000000000213 | VENEZIA_FUSINA_VIA_DEI_CANTIERI | 45.431 | 12.251 | 400000 | 355330 | YES | 2220.8125 | 7106.6 | 5329.95 | 10659.9 | 12880.7125 | 77284.275 | ITH3 | B
IT | ITH35 |  | IT05000000000215 | SANTO_STINO_DI_LIVENZA_CANALETTA | 45.731 | 12.697 | 10000 | 8083 | NO | 50.5188 | 0 | 0 | 0 | 293.0088 | 1758.0525 | ITH3 | B
IT | ITH36 |  | IT05000000000218 | ABANO_VIA_MONTEGROTTO | 45.341 | 11.771 | 35000 | 27839 | NO | 173.9938 | 0 | 0 | 0 | 1009.1638 | 6054.9825 | ITH3 | A
IT | ITH36 |  | IT05000000000219 | AGNA_VIA_CIMITERO | 45.162 | 11.966 | 6200 | 3025 | NO | 18.9062 | 0 | 0 | 0 | 109.6562 | 657.9375 | ITH3 | B
IT | ITH36 |  | IT05000000000222 | BOARA_PISANI_VIA_ROMA | 45.117 | 11.765 | 7500 | 6473 | NO | 40.4563 | 0 | 0 | 0 | 234.6463 | 1407.8775 | ITH3 | A
IT | ITH36 |  | IT05000000000226 | CARMIGNANO_DI_BRENTA_VIA_OSPITALE | 45.622 | 11.724 | 20000 | 11951 | NO | 74.6938 | 0 | 0 | 0 | 433.2237 | 2599.3425 | ITH3 | B
IT | ITH36 |  | IT05000000000227 | CASALSERUGO_VIA_L_DA_VINCI | 45.308 | 11.915 | 5000 | 4564 | NO | 28.525 | 0 | 0 | 0 | 165.445 | 992.67 | ITH3 | A
IT | ITH31 |  | IT05000000000010 | COLOGNA_VENETA_VIA_TRAVERSINA | 45.291 | 11.381 | 45000 | 23623 | NO | 147.6438 | 0 | 0 | 0 | 856.3338 | 5138.0025 | ITH3 | C
IT | ITH31 |  | IT05000000000012 | ISOLA_DELLA_SCALA_GIARELLA | 45.264 | 11.003 | 6000 | 6000 | NO | 37.5 | 0 | 0 | 0 | 217.5 | 1305 | ITH3 | A
IT | ITH31 |  | IT05000000000015 | OPPEANO_CASOTTON | 45.302 | 11.195 | 6000 | 5060 | NO | 31.625 | 0 | 0 | 0 | 183.425 | 1100.55 | ITH3 | B
IT | ITH31 |  | IT05000000000017 | LEGNAGO_PORTO | 45.186 | 11.334 | 7000 | 6890 | NO | 43.0625 | 0 | 0 | 0 | 249.7625 | 1498.575 | ITH3 | C
IT | ITH31 |  | IT05000000000018 | LEGNAGO_VANGADIZZA | 45.157 | 11.287 | 40000 | 43396 | NO | 271.225 | 0 | 0 | 0 | 1573.105 | 9438.63 | ITH3 | C
IT | ITH31 |  | IT05000000000019 | MOZZECANE_SAN_FAUSTINO | 45.299 | 10.819 | 6500 | 6031 | NO | 37.6938 | 0 | 0 | 0 | 218.6238 | 1311.7425 | ITH3 | B
IT | ITH31 |  | IT05000000000022 | AFFI_COSTABELLA | 45.549 | 10.78 | 9500 | 7250 | NO | 45.3125 | 0 | 0 | 0 | 262.8125 | 1576.875 | ITH3 | B
IT | ITH31 |  | IT05000000000023 | PESCHIERA_DEL_GARDA_PARADISO | 45.424 | 10.702 | 330000 | 160492 | YES | 1003.075 | 3209.84 | 2407.38 | 4814.76 | 5817.835 | 34907.01 | ITH3 | C
IT | ITH31 |  | IT05000000000024 | POVEGLIANO_VERONESE_VIA_NOGAROLE_ROCCA | 45.337 | 10.887 | 35000 | 35000 | NO | 218.75 | 0 | 0 | 0 | 1268.75 | 7612.5 | ITH3 | B
IT | ITH31 |  | IT05000000000026 | SAN_BONIFACIO_PALU | 45.388 | 11.276 | 60000 | 49657 | NO | 310.3562 | 0 | 0 | 0 | 1800.0662 | 10800.3975 | ITH3 | B
IT | ITH31 |  | IT05000000000027 | SAN_GIOVANNI_LUPATOTO_PALUSTRELLA | 45.371 | 11.059 | 24000 | 24000 | NO | 150 | 0 | 0 | 0 | 870 | 5220 | ITH3 | B
IT | ITH31 |  | IT05000000000031 | SAN_PIETRO_IN_CARIANO_NASSAR | 45.484 | 10.927 | 20000 | 17032 | NO | 106.45 | 0 | 0 | 0 | 617.41 | 3704.46 | ITH3 | B
IT | ITH31 |  | IT05000000000032 | SOMMACAMPAGNA_VIA_DELL_INDUSTRIA | 45.392 | 10.842 | 36000 | 28389 | NO | 177.4313 | 0 | 0 | 0 | 1029.1012 | 6174.6075 | ITH3 | B
IT | ITH31 |  | IT05000000000033 | VERONA_VIA_AVESANI | 45.418 | 10.996 | 410000 | 338619 | YES | 2116.3688 | 6772.38 | 5079.285 | 10158.57 | 12274.9387 | 73649.6325 | ITH3 | A
IT | ITH31 |  | IT05000000000034 | VIGASIO_CORSO_GARIBALDI | 45.313 | 10.945 | 7800 | 6143 | NO | 38.3938 | 0 | 0 | 0 | 222.6838 | 1336.1025 | ITH3 | A
IT | ITH34 |  | IT05000000000147 | CONEGLIANO_VIA_CA_DI_VILLA_CAMPOLONGO | 45.866 | 12.326 | 70000 | 42046 | NO | 262.7875 | 0 | 0 | 0 | 1524.1675 | 9145.005 | ITH3 | B
IT | ITH37 |  | IT05000000000275 | CASTELMASSA_VIA_SARTA | 45.003 | 11.333 | 50000 | 31283 | NO | 195.5187 | 0 | 0 | 0 | 1134.0087 | 6804.0525 | ITH3 | C
IT | ITH37 |  | IT05000000000280 | LENDINARA_VIA_CA_MOROSINI | 45.092 | 11.602 | 9000 | 7557 | NO | 47.2312 | 0 | 0 | 0 | 273.9412 | 1643.6475 | ITH3 | A
IT | ITH37 |  | IT05000000000282 | OCCHIOBELLO_VIALE_STAZIONE | 44.896 | 11.617 | 12000 | 9980 | NO | 62.375 | 0 | 0 | 0 | 361.775 | 2170.65 | ITH3 | A
IT | ITH37 |  | IT05000000000291 | PORTO_TOLLE_VIA_TANGENZIALE_EST | 44.942 | 12.325 | 6000 | 4405 | NO | 27.5312 | 0 | 0 | 0 | 159.6812 | 958.0875 | ITH3 | A
IT | ITH37 |  | IT05000000000293 | PORTO_VIRO_OVEST_S_S_ROMEA | 45.014 | 12.244 | 50000 | 25587 | NO | 159.9188 | 0 | 0 | 0 | 927.5288 | 5565.1725 | ITH3 | A
IT | ITH37 |  | IT05000000000299 | ROVIGO_S_APOLLINARE | 45.042 | 11.837 | 74500 | 46950 | NO | 293.4375 | 0 | 0 | 0 | 1701.9375 | 10211.625 | ITH3 | B
IT | ITH37 |  | IT05000000000301 | TRECENTA_VIA_BERETTARE | 45.025 | 11.469 | 5500 | 3700 | NO | 23.125 | 0 | 0 | 0 | 134.125 | 804.75 | ITH3 | B
IT | ITH37 |  | IT05000000000303 | ADRIA_VIA_RETRATTO | 45.046 | 12.05 | 20000 | 15030 | NO | 93.9375 | 0 | 0 | 0 | 544.8375 | 3269.025 | ITH3 | A
IT | ITH37 |  | IT05000000000304 | ROSOLINA_MARE_VIA_FOCI_ADIGE | 45.15 | 12.327 | 30000 | 19601 | NO | 122.5063 | 0 | 0 | 0 | 710.5362 | 4263.2175 | ITH3 | C
IT | ITH34 |  | IT05Q11000000000 | SAN_VENDEMIANO_VIA_FONTANE | 45.878 | 12.383 | 12500 | 8926 | NO | 55.7875 | 0 | 0 | 0 | 323.5675 | 1941.405 | ITH3 | C
IT | ITH34 |  | IT05Q150000000118010 | DEPURATORE_DI_RONCADE_SAN_CIPRIANO_VIA_MARCONI | 45.603 | 12.374 | 8000 | 4114 | NO | 25.7125 | 0 | 0 | 0 | 149.1325 | 894.795 | ITH3 | C
IT | ITH34 |  | IT05Q90000003408 | SERNAGLIA_DELLA_BATTAGLIA_VIA_CAL_DEL_SOLIGO | 45.86 | 12.179 | 9500 | 9185 | NO | 57.4062 | 0 | 0 | 0 | 332.9563 | 1997.7375 | ITH3 | B
IT | ITH34 |  | IT05000000000160 | PONTE_DI_PIAVE_VIA_RISORGIMENTO | 45.715 | 12.458 | 14000 | 6281 | NO | 39.2563 | 0 | 0 | 0 | 227.6863 | 1366.1175 | ITH3 | A
IT | ITH34 |  | IT05000000000161 | PREGANZIOL_VIA_SCHIAVONIA | 45.59 | 12.242 | 13000 | 12606 | NO | 78.7875 | 0 | 0 | 0 | 456.9675 | 2741.805 | ITH3 | C
IT | ITH34 |  | IT05000000000163 | QUINTO_DI_TREVISO_VIA_NOGARE_ | 45.641 | 12.176 | 11000 | 6813 | NO | 42.5813 | 0 | 0 | 0 | 246.9712 | 1481.8275 | ITH3 | B
IT | ITH34 |  | IT05000000000164 | PAESE_VIA_BRONDI | 45.667 | 12.171 | 45000 | 16062 | NO | 100.3875 | 0 | 0 | 0 | 582.2475 | 3493.485 | ITH3 | A
IT | ITH34 |  | IT05000000000166 | FARRA_DI_SOLIGO_VIA_BOSCHET | 45.893 | 12.119 | 5000 | 4834 | NO | 30.2125 | 0 | 0 | 0 | 175.2325 | 1051.395 | ITH3 | C
IT | ITH34 |  | IT05000000000168 | SILEA_VIA_SILE | 45.65 | 12.298 | 8000 | 6102 | NO | 38.1375 | 0 | 0 | 0 | 221.1975 | 1327.185 | ITH3 | A
IT | ITH34 |  | IT05000000000169 | TREVISO_SANT_ANTONINO,_VIA_PAVESE | 45.649 | 12.276 | 70000 | 71728 | NO | 448.3 | 0 | 0 | 0 | 2600.14 | 15600.84 | ITH3 | B
IT | ITH34 |  | IT05000000000170 | VALDOBBIADENE_BIGOLINO,_VIA_DEI_FAVERI | 45.863 | 12.027 | 10000 | 7215 | NO | 45.0938 | 0 | 0 | 0 | 261.5437 | 1569.2625 | ITH3 | A
IT | ITH34 |  | IT05000000000172 | ZERO_BRANCO_VIA_MILAN | 45.59 | 12.175 | 5000 | 3899 | NO | 24.3688 | 0 | 0 | 0 | 141.3388 | 848.0325 | ITH3 | C
IT | ITH35 |  | IT05000000000180 | CAORLE_PALANGON | 45.614 | 12.888 | 120000 | 70052 | NO | 437.825 | 0 | 0 | 0 | 2539.385 | 15236.31 | ITH3 | A
IT | ITH35 |  | IT05000000000181 | CAVALLINO_TREPORTI_CAVALLINO | 45.459 | 12.487 | 105000 | 78507 | NO | 490.6688 | 0 | 0 | 0 | 2845.8787 | 17075.2725 | ITH3 | C
IT | ITH35 |  | IT05000000000183 | CAVARZERE_CAVARZERE_VIA_PIANTAZZA | 45.133 | 12.097 | 20000 | 9090 | NO | 56.8125 | 0 | 0 | 0 | 329.5125 | 1977.075 | ITH3 | B
IT | ITC33 |  | IT07Q13000000001 | S_STEFANO_D_AVETO_CAPOLUOGO | 44.5462 | 9.4432 | 5400 | 4400 | NO | 27.5 | 0 | 0 | 0 | 159.5 | 957 | ITC3 | C
IT | ITC32 |  | IT070000000018 | CONSORZIO_SAVONA | 44.2881 | 8.4406 | 434370 | 264551 | YES | 1653.4438 | 5291.02 | 3968.265 | 7936.53 | 9589.9738 | 57539.8425 | ITC3 | A
IT | ITC32 |  | IT070000000016 | CONSORZIO_VALBORMIDA | 44.4586 | 8.3076 | 90000 | 30100 | NO | 188.125 | 0 | 0 | 0 | 1091.125 | 6546.75 | ITC3 | C
IT | ITC33 |  | IT070000000031 | PEGLI | 44.4239 | 8.8216 | 40000 | 40000 | NO | 250 | 0 | 0 | 0 | 1450 | 8700 | ITC3 | A
IT | ITC33 |  | IT070000000030 | PRA_VOLTRI | 44.4262 | 8.7625 | 61500 | 61500 | NO | 384.375 | 0 | 0 | 0 | 2229.375 | 13376.25 | ITC3 | B
IT | ITC33 |  | IT070000000001 | PRELI | 44.3219 | 9.307 | 33000 | 33000 | NO | 206.25 | 0 | 0 | 0 | 1196.25 | 7177.5 | ITC3 | A
IT | ITH35 |  | IT05000000000184 | CEGGIA_CAPOLUOGO | 45.683 | 12.629 | 5000 | 5196 | NO | 32.475 | 0 | 0 | 0 | 188.355 | 1130.13 | ITH3 | A
IT | ITH35 |  | IT05000000000185 | CHIOGGIA_BRONDOLO | 45.2 | 12.27 | 165000 | 75179 | YES | 469.8688 | 1503.58 | 1127.685 | 2255.37 | 2725.2387 | 16351.4325 | ITH3 | A
IT | ITH35 |  | IT05000000000186 | CONA_PEGOLOTTE | 45.194 | 12.031 | 6000 | 3504 | NO | 21.9 | 0 | 0 | 0 | 127.02 | 762.12 | ITH3 | B
IT | ITH35 |  | IT05000000000188 | ERACLEA_ERACLEA_MARE_VIA_DEI_PIOPPI | 45.553 | 12.741 | 32000 | 15009 | NO | 93.8062 | 0 | 0 | 0 | 544.0762 | 3264.4575 | ITH3 | C
IT | ITH35 |  | IT05000000000190 | JESOLO_VIA_ALEARDI | 45.505 | 12.617 | 185000 | 120577 | YES | 753.6062 | 2411.54 | 1808.655 | 3617.31 | 4370.9162 | 26225.4975 | ITH3 | A
IT | ITH36 |  | IT05000000000236 | ESTE_VIA_PRA | 45.211 | 11.647 | 25000 | 19140 | NO | 119.625 | 0 | 0 | 0 | 693.825 | 4162.95 | ITH3 | B
IT | ITH36 |  | IT05000000000237 | GRANTORTO_VIA_S_ANTONIO | 45.598 | 11.736 | 8000 | 3034 | NO | 18.9625 | 0 | 0 | 0 | 109.9825 | 659.895 | ITH3 | A
IT | ITH36 |  | IT05000000000238 | VILLAFRANCA_PADOVANA_VIA_FIRENZE,_LOC_TAGGI_DI_SOPRA | 45.473 | 11.811 | 12000 | 9510 | NO | 59.4375 | 0 | 0 | 0 | 344.7375 | 2068.425 | ITH3 | B
IT | ITH36 |  | IT05000000000239 | LIMENA_VIA_A_VOLTA | 45.466 | 11.861 | 20000 | 15851 | NO | 99.0688 | 0 | 0 | 0 | 574.5987 | 3447.5925 | ITH3 | B
IT | ITH36 |  | IT05000000000240 | MASERA_VIA_ROMA | 45.317 | 11.875 | 5933 | 5930 | NO | 37.0625 | 0 | 0 | 0 | 214.9625 | 1289.775 | ITH3 | B
IT | ITH36 |  | IT05000000000246 | MESTRINO_VIA_PETRARCA | 45.428 | 11.767 | 12800 | 12056 | NO | 75.35 | 0 | 0 | 0 | 437.03 | 2622.18 | ITH3 | B
IT | ITH36 |  | IT05000000000247 | MONSELICE_VIA_DEL_BORGO | 45.223 | 11.764 | 40000 | 17569 | NO | 109.8062 | 0 | 0 | 0 | 636.8762 | 3821.2575 | ITH3 | B
IT | ITH36 |  | IT05000000000248 | MONTAGNANA_VIA_CHISOGNO,_LOC_CHISOGNO | 45.233 | 11.479 | 12000 | 11155 | NO | 69.7188 | 0 | 0 | 0 | 404.3687 | 2426.2125 | ITH3 | B
IT | ITH36 |  | IT05000000000249 | PADOVA_VIA_PONTEDERA,_LOC_GUIZZA | 45.378 | 11.879 | 13000 | 12480 | NO | 78 | 0 | 0 | 0 | 452.4 | 2714.4 | ITH3 | A
IT | ITH36 |  | IT05000000000250 | ALBIGNASEGO_VIA_TORINO | 45.347 | 11.878 | 40000 | 38400 | NO | 240 | 0 | 0 | 0 | 1392 | 8352 | ITH3 | B
IT | ITH36 |  | IT05000000000251 | PADOVA_VIA_A_PEDANIO,_LOCALITA_CA_NORDIO | 45.383 | 11.914 | 197000 | 212885 | YES | 1330.5312 | 4257.7 | 3193.275 | 6386.55 | 7717.0813 | 46302.4875 | ITH3 | A
IT | ITH36 |  | IT05000000000252 | PERNUMIA_VIA_BEVARARA | 45.262 | 11.792 | 7500 | 7439 | NO | 46.4938 | 0 | 0 | 0 | 269.6638 | 1617.9825 | ITH3 | A
IT | ITH36 |  | IT05000000000254 | PONTELONGO_VIA_DANTE | 45.24 | 12.031 | 6000 | 3935 | NO | 24.5938 | 0 | 0 | 0 | 142.6437 | 855.8625 | ITH3 | A
IT | ITH36 |  | IT05000000000255 | POZZONOVO_VIA_VALLASE | 45.186 | 11.796 | 14700 | 3596 | NO | 22.475 | 0 | 0 | 0 | 130.355 | 782.13 | ITH3 | B
IT | ITH36 |  | IT05000000000256 | SELVAZZANO_VIA_MONTEGRAPPA | 45.38 | 11.802 | 27500 | 26045 | NO | 162.7812 | 0 | 0 | 0 | 944.1312 | 5664.7875 | ITH3 | B
IT | ITH36 |  | IT05000000000257 | SANTA_MARGHERITA_D_ADIGE_VIA_GRANZE | 45.206 | 11.572 | 19000 | 9217 | NO | 57.6062 | 0 | 0 | 0 | 334.1162 | 2004.6975 | ITH3 | C
IT | ITH36 |  | IT05000000000258 | SOLESINO_VIA_TIEPOLO | 45.163 | 11.752 | 12250 | 10981 | NO | 68.6313 | 0 | 0 | 0 | 398.0613 | 2388.3675 | ITH3 | C
IT | ITH36 |  | IT05000000000261 | VIGONZA_VIA_BARBARIGO | 45.424 | 11.992 | 70000 | 42381 | NO | 264.8813 | 0 | 0 | 0 | 1536.3112 | 9217.8675 | ITH3 | B
IT | ITH36 |  | IT05000000000263 | TORREGLIA_VIA_BOSCHETTE | 45.333 | 11.744 | 5000 | 3575 | NO | 22.3438 | 0 | 0 | 0 | 129.5938 | 777.5625 | ITH3 | B
IT | ITH36 |  | IT05000000000264 | BATTAGLIA_TERME_VIA_SELVATICHE | 45.279 | 11.772 | 10000 | 7150 | NO | 44.6875 | 0 | 0 | 0 | 259.1875 | 1555.125 | ITH3 | C
IT | ITH36 |  | IT05000000000265 | MONTEGROTTO_TERME_VIA_FRATELLI_BANDIERA | 45.313 | 11.791 | 20000 | 14300 | NO | 89.375 | 0 | 0 | 0 | 518.375 | 3110.25 | ITH3 | C
IT | ITH36 |  | IT05000000000266 | RUBANO_VIA_MAZZINI | 45.425 | 11.825 | 22000 | 16471 | NO | 102.9438 | 0 | 0 | 0 | 597.0738 | 3582.4425 | ITH3 | A
IT | ITH36 |  | IT05000000000267 | CERVARESE_SANTA_CROCE_VIA_XX_SETTEMBRE_MONTEMERLO | 45.374 | 11.715 | 7000 | 6910 | NO | 43.1875 | 0 | 0 | 0 | 250.4875 | 1502.925 | ITH3 | B
IT | ITH36 |  | IT05000000000268 | PONTE_SAN_NICOLO_VIA_S_ANTONIO_LOCALITA_RIO | 45.36 | 11.923 | 18000 | 17280 | NO | 108 | 0 | 0 | 0 | 626.4 | 3758.4 | ITH3 | B
IT | ITH36 |  | IT05000000000269 | CADONEGHE_VIA_MATTEOTTI | 45.44 | 11.914 | 50000 | 47362 | NO | 296.0125 | 0 | 0 | 0 | 1716.8725 | 10301.235 | ITH3 | B
IT | ITH37 |  | IT05000000000270 | ARIANO_POLESINE_VIA_BRENTA | 44.945 | 12.135 | 9500 | 2526 | NO | 15.7875 | 0 | 0 | 0 | 91.5675 | 549.405 | ITH3 | B
IT | ITH37 |  | IT05000000000271 | BADIA_POLESINE_VIA_CA_MIGNOLA | 45.094 | 11.51 | 25000 | 8618 | NO | 53.8625 | 0 | 0 | 0 | 312.4025 | 1874.415 | ITH3 | A
IT | ITH33 |  | IT05Q170000000059010 | D_FALCADE_LOC_CAVIOLA | 46.362 | 11.9 | 9700 | 5818 | NO | 36.3625 | 0 | 0 | 0 | 210.9025 | 1265.415 | ITH3 | B
IT | ITH32 |  | IT05Q90000003274 | LONGARE_PONTE_COSTOZZA | 45.464 | 11.607 | 5400 | 4154 | NO | 25.9625 | 0 | 0 | 0 | 150.5825 | 903.495 | ITH3 | B
IT | ITH36 |  | IT05Q90000003287 | SANT_URBANO_LOC_CA_BRUSA | 45.138 | 11.599 | 6600 | 3860 | NO | 24.125 | 0 | 0 | 0 | 139.925 | 839.55 | ITH3 | C
IT | ITH36 |  | IT05Q90000003324 | CAMPOSAMPIERO_VIA_STRAELLE_BIOTRATTAMENTO | 45.554 | 11.956 | 70000 | 41179 | YES | 257.3688 | 823.58 | 617.685 | 1235.37 | 1492.7387 | 8956.4325 | ITH3 | B
IT | ITH35 |  | IT05Q90000003343 | IMPIANTI_A_SERVIZIO_DEL_CENTRO_STORICO_DI_VENEZIA | 45.438 | 12.335 | 52667 | 52667 | NO | 329.1687 | 0 | 0 | 0 | 1909.1787 | 11455.0725 | ITH3 | A
IT | ITH37 |  | IT05Q90000003355 | DEPURATORE_PRIVATO_DELL_ISOLA_DI_ALBARELLA_ROSOLINA | 45.088 | 12.335 | 12600 | 9481 | NO | 59.2563 | 0 | 0 | 0 | 343.6863 | 2062.1175 | ITH3 | C
IT | ITC31 |  | IT070000000009 | VALLECROSIA | 43.7837 | 7.6344 | 35000 | 35000 | NO | 218.75 | 0 | 0 | 0 | 1268.75 | 7612.5 | ITC3 | B
IT | ITC32 |  | IT070000000058 | VILLAFONTANA | 43.9509 | 8.1549 | 60000 | 20693 | NO | 129.3313 | 0 | 0 | 0 | 750.1212 | 4500.7275 | ITC3 | A
IT | ITC33 |  | IT070000000046 | VALPOCEVERA | 44.4165 | 8.8787 | 160000 | 125000 | YES | 781.25 | 2500 | 1875 | 3750 | 4531.25 | 27187.5 | ITC3 | A
IT | ITC33 |  | IT070000000042 | CIAZZE | 44.2188 | 9.5087 | 7000 | 2800 | NO | 17.5 | 0 | 0 | 0 | 101.5 | 609 | ITC3 | B
IT | ITC33 |  | IT070000000033 | DARSENA | 44.4138 | 8.9238 | 220000 | 220000 | NO | 1375 | 0 | 0 | 0 | 7975 | 47850 | ITC3 | B
IT | ITH34 |  | IT05Q90000003384 | MOTTA_DI_LIVENZA_VIA_CALLUNGA_ZI_SUD | 45.742 | 12.618 | 31550 | 11134 | NO | 69.5875 | 0 | 0 | 0 | 403.6075 | 2421.645 | ITH3 | B
IT | ITH31 |  | IT05Q90000003436 | SAN_PIETRO_DI_MORUBIO_VIA_BELBROLO | 45.242 | 11.217 | 6000 | 3161 | NO | 19.7563 | 0 | 0 | 0 | 114.5862 | 687.5175 | ITH3 | B
IT | ITI11 |  | IT09RT0518 | IDL_FOSSA_MAESTRA | 44.0497 | 10.0221 | 45000 | 42790 | NOT KNOWN | 267.4375 | 0 | 0 | 0 | 1551.1375 | 9306.825 | ITC3 | A
IT | ITC34 |  | IT070000000024 | DEPURATORE_CAMISANO | 44.0798 | 9.9618 | 60000 | 27608 | NO | 172.55 | 0 | 0 | 0 | 1000.79 | 6004.74 | ITC3 | C
IT | ITC34 |  | IT070000000019 | PADULETTI | 44.0913 | 10.0056 | 7500 | 6579 | NO | 41.1187 | 0 | 0 | 0 | 238.4887 | 1430.9325 | ITC3 | A
IT | ITC34 |  | IT070000000020 | DEPURATORE_PIANO_DI_FOLLO | 44.1631 | 9.8685 | 11000 | 3706 | NO | 23.1625 | 0 | 0 | 0 | 134.3425 | 806.055 | ITC3 | A
IT | ITC34 |  | IT070000000011 | STAGNONI | 44.1109 | 9.8596 | 100000 | 88848 | YES | 555.3 | 1776.96 | 1332.72 | 2665.44 | 3220.74 | 19324.44 | ITC3 | A
IT | ITC34 |  | IT070000000021 | DEPURATORE_LOC_PORTONETTI | 44.0574 | 10.0255 | 18000 | 6450 | NO | 40.3125 | 0 | 0 | 0 | 233.8125 | 1402.875 | ITC3 | B
IT | ITC34 |  | IT070000000023 | DEP_LOC_GHIARETTOLO | 44.139 | 9.9116 | 9933 | 5133 | NO | 32.0813 | 0 | 0 | 0 | 186.0712 | 1116.4275 | ITC3 | B
IT | ITC34 |  | IT070000000012 | DEP_LOC_SILEA | 44.0987 | 9.9616 | 21000 | 18118 | NO | 113.2375 | 0 | 0 | 0 | 656.7775 | 3940.665 | ITC3 | A
IT | ITC34 |  | IT07Q13000000002 | DEIVA_MARINA_LOC_FORNACE | 44.2142 | 9.5182 | 16274 | 6239 | NO | 38.9937 | 0 | 0 | 0 | 226.1637 | 1356.9825 | ITC3 | A
IT | ITC34 |  | IT07Q170000001 | MONTEROSSO_FEGINA | 44.1447 | 9.6443 | 5800 | 2733 | NO | 17.0813 | 0 | 0 | 0 | 99.0712 | 594.4275 | ITC3 | C
IT | ITC34 |  | IT07Q170000002 | LEVANTO_CAPOLUOGO | 44.1721 | 9.6066 | 25000 | 8942 | NO | 55.8875 | 0 | 0 | 0 | 324.1475 | 1944.885 | ITC3 | A
IT | ITC33 |  | IT070000000032 | SESTRI_PONENTE | 44.4166 | 8.8492 | 130000 | 130000 | YES | 812.5 | 2600 | 1950 | 3900 | 4712.5 | 28275 | ITC3 | B
IT | ITC33 |  | IT070000000036 | SORI | 44.371 | 9.1025 | 10000 | 3150 | NO | 19.6875 | 0 | 0 | 0 | 114.1875 | 685.125 | ITC3 | A
IT | ITH20 |  | IT220000000008 | DEPURATORE_DI_ARCO | 45.8803 | 10.882 | 25700 | 33976 | NO | 212.35 | 0 | 0 | 0 | 1231.63 | 7389.78 | ITH2 | B
IT | ITH20 |  | IT220000000009 | DEPURATORE_DI_AVIO | 45.7305 | 10.9463 | 8000 | 3563 | NO | 22.2688 | 0 | 0 | 0 | 129.1587 | 774.9525 | ITH2 | B
IT | ITH20 |  | IT220000000010 | DEPURATORE_DI_BASELGA_DI_PINE | 46.1269 | 11.2334 | 10000 | 9040 | NO | 56.5 | 0 | 0 | 0 | 327.7 | 1966.2 | ITH2 | A
IT | ITH20 |  | IT220000000012 | DEPURATORE_DI_CALAVINO | 46.0569 | 10.9796 | 7000 | 5357 | NO | 33.4813 | 0 | 0 | 0 | 194.1913 | 1165.1475 | ITH2 | C
IT | ITH20 |  | IT220000000013 | DEPURATORE_DI_CAMPITELLO_DI_FASSA | 46.4715 | 11.7389 | 20000 | 16830 | NO | 105.1875 | 0 | 0 | 0 | 610.0875 | 3660.525 | ITH2 | B
IT | ITH20 |  | IT220000000014 | DEPURATORE_DI_CAMPODENNO | 46.2488 | 11.0604 | 20000 | 12030 | NO | 75.1875 | 0 | 0 | 0 | 436.0875 | 2616.525 | ITH2 | C
IT | ITH20 |  | IT220000000015 | DEPURATORE_DI_CANAL_SAN_BOVO | 46.1513 | 11.7277 | 10000 | 2378 | NO | 14.8625 | 0 | 0 | 0 | 86.2025 | 517.215 | ITH2 | B
IT | ITH20 |  | IT220000000017 | DEPURATORE_DI_CASTELLO_DI_FIEMME | 46.2796 | 11.4459 | 30000 | 21620 | NO | 135.125 | 0 | 0 | 0 | 783.725 | 4702.35 | ITH2 | B
IT | ITH20 |  | IT220000000018 | DEPURATORE_DI_CASTELLO_TESINO | 46.0589 | 11.6299 | 7500 | 5624 | NO | 35.15 | 0 | 0 | 0 | 203.87 | 1223.22 | ITH2 | A
IT | ITH20 |  | IT220000000019 | DEPURATORE_DI_CAVARENO | 46.3999 | 11.1308 | 20000 | 17164 | NO | 107.275 | 0 | 0 | 0 | 622.195 | 3733.17 | ITH2 | B
IT | ITH20 |  | IT220000000020 | DEPURATORE_DI_CHIZZOLA | 45.8015 | 11.0155 | 30000 | 11956 | NO | 74.725 | 0 | 0 | 0 | 433.405 | 2600.43 | ITH2 | B
IT | ITH20 |  | IT220000000021 | DEPURATORE_DI_CLES | 46.3495 | 11.0502 | 15000 | 14035 | NO | 87.7188 | 0 | 0 | 0 | 508.7687 | 3052.6125 | ITH2 | A
IT | ITH20 |  | IT22Q13000000001 | DEPURATORE_DI_DIMARO | 46.3287 | 10.881 | 20000 | 7689 | NO | 48.0563 | 0 | 0 | 0 | 278.7263 | 1672.3575 | ITH2 | A
IT | ITH20 |  | IT220000000022 | DEPURATORE_DI_DORSINO | 46.0689 | 10.8948 | 6000 | 4696 | NO | 29.35 | 0 | 0 | 0 | 170.23 | 1021.38 | ITH2 | C
IT | ITH20 |  | IT220000000023 | DEPURATORE_DI_FAI_DELLA_PAGANELLA | 46.1795 | 11.0771 | 5200 | 5606 | NO | 35.0375 | 0 | 0 | 0 | 203.2175 | 1219.305 | ITH2 | B
IT | ITH20 |  | IT220000000026 | DEPURATORE_DI_FOLGARIA | 45.9077 | 11.1517 | 24000 | 16222 | NO | 101.3875 | 0 | 0 | 0 | 588.0475 | 3528.285 | ITH2 | C
IT | ITH20 |  | IT22Q13000000000 | DEPURATORE_DI_FONDO | 46.4356 | 11.13 | 10000 | 3284 | NO | 20.525 | 0 | 0 | 0 | 119.045 | 714.27 | ITH2 | B
IT | ITH20 |  | IT220000000027 | DEPURATORE_DI_GIUSTINO | 46.1502 | 10.7631 | 30000 | 25076 | NO | 156.725 | 0 | 0 | 0 | 909.005 | 5454.03 | ITH2 | B
IT | ITH20 |  | IT220000000037 | DEPURATORE_DI_MEZZANA | 46.3157 | 10.813 | 30000 | 22326 | NO | 139.5375 | 0 | 0 | 0 | 809.3175 | 4855.905 | ITH2 | C
IT | ITH20 |  | IT220000000038 | DEPURATORE_DI_MEZZOCORONA | 46.2037 | 11.1362 | 26500 | 17620 | NO | 110.125 | 0 | 0 | 0 | 638.725 | 3832.35 | ITH2 | B
IT | ITH20 |  | IT220000000040 | DEPURATORE_DI_MOENA | 46.3584 | 11.6441 | 17000 | 11429 | NO | 71.4313 | 0 | 0 | 0 | 414.3013 | 2485.8075 | ITH2 | C
IT | ITH20 |  | IT220000000041 | DEPURATORE_DI_MOLINA_DI_FIEMME | 46.268 | 11.4115 | 7500 | 2973 | NO | 18.5813 | 0 | 0 | 0 | 107.7712 | 646.6275 | ITH2 | B
IT | ITH20 |  | IT220000000043 | DEPURATORE_DI_MOLVENO | 46.138 | 10.9663 | 10000 | 9300 | NO | 58.125 | 0 | 0 | 0 | 337.125 | 2022.75 | ITH2 | B
IT | ITH20 |  | IT220000000045 | DEPURATORE_DI_MORI | 45.8493 | 10.9955 | 20000 | 13422 | NO | 83.8875 | 0 | 0 | 0 | 486.5475 | 2919.285 | ITH2 | B
IT | ITH20 |  | IT220000000046 | DEPURATORE_DI_PASSO_TONALE | 46.2587 | 10.6047 | 10000 | 10000 | NO | 62.5 | 0 | 0 | 0 | 362.5 | 2175 | ITH2 | C
IT | ITH20 |  | IT220000000047 | DEPURATORE_DI_PIETRAMURATA | 46.0112 | 10.9531 | 5000 | 2647 | NO | 16.5437 | 0 | 0 | 0 | 95.9537 | 575.7225 | ITH2 | C
IT | ITH20 |  | IT220000000048 | DEPURATORE_DI_PIEVE_DI_BONO | 45.9269 | 10.6329 | 11000 | 8611 | NO | 53.8188 | 0 | 0 | 0 | 312.1488 | 1872.8925 | ITH2 | C
IT | ITH20 |  | IT220000000049 | DEPURATORE_DI_PIEVE_DI_LEDRO | 45.8814 | 10.7337 | 13500 | 13172 | NO | 82.325 | 0 | 0 | 0 | 477.485 | 2864.91 | ITH2 | B
IT | ITH20 |  | IT220000000051 | DEPURATORE_DI_POZZA_DI_FASSA | 46.4192 | 11.6843 | 40000 | 21097 | NO | 131.8563 | 0 | 0 | 0 | 764.7663 | 4588.5975 | ITH2 | A
IT | ITH20 |  | IT220000000052 | DEPURATORE_DI_RAGOLI | 46.0528 | 10.7892 | 30000 | 16678 | NO | 104.2375 | 0 | 0 | 0 | 604.5775 | 3627.465 | ITH2 | C
IT | ITH20 |  | IT220000000053 | DEPURATORE_DI_RIVA_ARENA | 45.8869 | 10.8563 | 50000 | 38650 | NO | 241.5625 | 0 | 0 | 0 | 1401.0625 | 8406.375 | ITH2 | A
IT | ITH20 |  | IT220000000054 | DEPURATORE_DI_RIVA_SAN_NICOLO | 45.8765 | 10.8569 | 16000 | 11305 | NO | 70.6562 | 0 | 0 | 0 | 409.8062 | 2458.8375 | ITH2 | B
IT | ITH20 |  | IT220000000056 | DEPURATORE_DI_ROVERETO | 45.8725 | 11.015 | 95000 | 82477 | YES | 515.4813 | 1649.54 | 1237.155 | 2474.31 | 2989.7913 | 17938.7475 | ITH2 | A
IT | ITH20 |  | IT22Q13000000002 | DEPURATORE_DI_SAN_MARTINO_DI_CASTROZZA_CAMOI | 46.24 | 11.8065 | 24000 | 9404 | NO | 58.775 | 0 | 0 | 0 | 340.895 | 2045.37 | ITH2 | C
IT | ITH20 |  | IT220000000059 | DEPURATORE_DI_SPIAZZO | 46.0929 | 10.7351 | 13000 | 12726 | NO | 79.5375 | 0 | 0 | 0 | 461.3175 | 2767.905 | ITH2 | B
IT | ITH20 |  | IT220000000072 | DEPURATORE_DI_STENICO | 46.0479 | 10.8958 | 20000 | 9334 | NO | 58.3375 | 0 | 0 | 0 | 338.3575 | 2030.145 | ITH2 | C
IT | ITH20 |  | IT220000000061 | DEPURATORE_DI_STORO | 45.8384 | 10.558 | 10000 | 5707 | NO | 35.6688 | 0 | 0 | 0 | 206.8788 | 1241.2725 | ITH2 | B
IT | ITH20 |  | IT220000000062 | DEPURATORE_DI_TAIO | 46.3156 | 11.0605 | 20000 | 19505 | NO | 121.9062 | 0 | 0 | 0 | 707.0562 | 4242.3375 | ITH2 | B
IT | ITH20 |  | IT220000000063 | DEPURATORE_DI_TESERO | 46.2841 | 11.5074 | 50000 | 24427 | NO | 152.6688 | 0 | 0 | 0 | 885.4787 | 5312.8725 | ITH2 | A
IT | ITH20 |  | IT220000000064 | DEPURATORE_DI_TRENTO_NORD | 46.0816 | 11.1092 | 120000 | 117629 | YES | 735.1813 | 2352.58 | 1764.435 | 3528.87 | 4264.0513 | 25584.3075 | ITH2 | A
IT | ITH20 |  | IT220000000065 | DEPURATORE_DI_TRENTO_SUD | 46.0354 | 11.1236 | 100000 | 99866 | YES | 624.1625 | 1997.32 | 1497.99 | 2995.98 | 3620.1425 | 21720.855 | ITH2 | A
IT | ITH20 |  | IT220000000068 | DEPURATORE_DI_VILLA_AGNEDO | 46.0481 | 11.5141 | 30000 | 22933 | NO | 143.3313 | 0 | 0 | 0 | 831.3212 | 4987.9275 | ITH2 | B
IT | ITC33 |  | IT070000000003 | RAPALLO | 44.3505 | 9.2341 | 90000 | 30000 | NO | 187.5 | 0 | 0 | 0 | 1087.5 | 6525 | ITC3 | A
IT | ITC33 |  | IT070000000041 | RIVA_TRIGOSO | 44.2593 | 9.4179 | 38000 | 11000 | NO | 68.75 | 0 | 0 | 0 | 398.75 | 2392.5 | ITC3 | A
IT | ITC33 |  | IT070000000004 | RONCO_NORD | 44.6203 | 8.9444 | 44000 | 14700 | NO | 91.875 | 0 | 0 | 0 | 532.875 | 3197.25 | ITC3 | B
IT | ITC33 |  | IT070000000043 | ROSSIGLIONE | 44.573 | 8.6685 | 14000 | 14000 | NO | 87.5 | 0 | 0 | 0 | 507.5 | 3045 | ITC3 | B
IT | ITH20 |  | IT220000000004 | DEPURATORE_DI_ALA | 45.745 | 10.9846 | 10000 | 4448 | NO | 27.8 | 0 | 0 | 0 | 161.24 | 967.44 | ITH2 | C
IT | ITH20 |  | IT220000000007 | DEPURATORE_DI_ANDALO | 46.161 | 10.9982 | 10000 | 7768 | NO | 48.55 | 0 | 0 | 0 | 281.59 | 1689.54 | ITH2 | B
IT | ITC32 |  | IT070000000060 | EX_ACNA_CO | 44.3948 | 8.1781 | 11000 | 8800 | NO | 55 | 0 | 0 | 0 | 319 | 1914 | ITC3 | A
IT | ITC32 |  | IT070000000014 | LOC_ANTOGNANO | 44.053 | 8.2242 | 90000 | 37430 | YES | 233.9375 | 748.6 | 561.45 | 1122.9 | 1356.8375 | 8141.025 | ITC3 | B
IT | ITC32 |  | IT070000000015 | LOC_PATARELLO | 44.1153 | 8.2386 | 140000 | 165596 | NO | 1034.975 | 0 | 0 | 0 | 6002.855 | 36017.13 | ITC3 | A
IT | ITC32 |  | IT070000000059 | VIA_CRISPI | 44.1533 | 8.2843 | 70000 | 2156 | NO | 13.475 | 0 | 0 | 0 | 78.155 | 468.93 | ITC3 | A
IT | ITC32 |  | IT07Q13000000000 | CALIZZANO_CARAGNETTA | 44.2656 | 8.1198 | 9000 | 6000 | NO | 37.5 | 0 | 0 | 0 | 217.5 | 1305 | ITC3 | C
IT | ITC34 |  | IT070000000026 | DEPURATORE_CEPARANA | 44.1576 | 9.8847 | 10000 | 7922 | NO | 49.5125 | 0 | 0 | 0 | 287.1725 | 1723.035 | ITC3 | B
IT | ITI31 |  | IT11000000000018 | CAMPO_QUADRO_GBC_DEP | 43.9564 | 12.7503 | 49600 | 16945 | NOT KNOWN | 105.9062 | 0 | 0 | 0 | 614.2562 | 3685.5375 | ITH5 | A
IT | ITH20 |  | IT220000000029 | DEPURATORE_DI_IMER | 46.1415 | 11.7869 | 30000 | 25271 | NO | 157.9437 | 0 | 0 | 0 | 916.0737 | 5496.4425 | ITH2 | C
IT | ITH20 |  | IT220000000031 | DEPURATORE_DI_LAVARONE | 45.9321 | 11.265 | 12500 | 12122 | NO | 75.7625 | 0 | 0 | 0 | 439.4225 | 2636.535 | ITH2 | C
IT | ITH20 |  | IT220000000032 | DEPURATORE_DI_LAVIS | 46.1303 | 11.0819 | 30000 | 13878 | NO | 86.7375 | 0 | 0 | 0 | 503.0775 | 3018.465 | ITH2 | A
IT | ITH20 |  | IT220000000033 | DEPURATORE_DI_LEVICO | 46.003 | 11.3198 | 100000 | 60741 | NO | 379.6312 | 0 | 0 | 0 | 2201.8612 | 13211.1675 | ITH2 | B
IT | ITH20 |  | IT220000000034 | DEPURATORE_DI_MADONNA_DI_CAMPIGLIO | 46.2148 | 10.825 | 32000 | 31196 | NO | 194.975 | 0 | 0 | 0 | 1130.855 | 6785.13 | ITH2 | B
IT | ITH20 |  | IT220000000035 | DEPURATORE_DI_MALE | 46.3485 | 10.9171 | 12000 | 8655 | NO | 54.0938 | 0 | 0 | 0 | 313.7437 | 1882.4625 | ITH2 | B

## Meta
Field name | Field definition | Source | Note
rptMStateKey | Member State abbreviation | EEA, 2019
uwwNuts | internal numerical database code of Region (NUTS) | EEA, 2019
aggCode | internal numerical database code of agglomeration | EEA, 2019
uwwCode | ID of UWWTP / collecting system without treatment | EEA, 2019
uwwName | Name of UWWTP / collecting system without treatment | EEA, 2019
uwwLatitude | Latitude (ETRS89, decimal degrees) | EEA, 2019
uwwLongitude | Longitude (ETRS89, decimal degrees) | EEA, 2019
uwwCapacity | Organic design capacity (p.e.) | EEA, 2019
uwwLoadEntering | Load entering UWWTP (p.e.) | EEA, 2019
anaerobic digestion [y/n] | anaerobic sludge stabilization | expert judgement | yes / no
inflow [m³/h] | wastewater inflow | own calculation
digester gas [m³/d] | digester gas | own calculation
digester gas el. [MWh/a] | electric energy from digester gas combustion | own calculation
digester gas th. [MWh/a] | thermal energy from digester gas combustion | own calculation
heat recovery potential [kW] | wastewater heat recovery potential | own calculation
heat pump [MWh/a] | thermal energy from wastewater provided by heat pump | own calculation
NUTS_ID | internal numerical database code of Region (NUTS) | EC, Eurostat, GISCO, 2018
spatial context | spatial context of the WWTP | own calculation | A = within the settlement, B = near to settlement, C = far from the settlement

## Assumptions
Assumptions | Value | Source | Note
wastewater flow [l/PE*d] | 150 | own estimation
digester gas production [l/PE*d] | 20 | Lindtner, 2008 | in the range ov 15-22 l/PE*d
electric energy from digester gas [kWh/PE*a] | 15 | Lindtner, 2008 | in the range of 10-20 kWh/PE*a
thermal energy from digester gas [kWh/PE*a] | 30 | Lindtner, 2008 | in the range of 20-40 kWh/PE*a
heat capacity (waste)water [kWh/m³*K] | 1.16
wastewater temperature reduction heat exchanger [K] | 5 | own estimation
COP heat pump [-] | 4 | own estimation
heat pump operating hours [h/a] | 4500 | Neugebauer et al. 2015